## 遥测
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位
1 | BMS系统故障汇总 | U16 |  |  | 4097 | InputRegisters | 1 | AB | 1 | 0 |  | systemFaultSum |  |  | BMS内部通讯故障¦BMS internal communication fault¦2 PCS通讯故障报警¦PCS communication fault alarm¦2 PCS控制失效报警¦PCS control failure alarm¦2 EMS通信故障报警¦EMS communication fault alarm¦2 Rack间压差过大报警¦Excessive pressure difference between racks alarm¦2 簇间电流差一级告警¦Cluster current difference level 1 alarm¦2 紧急停机¦Emergency shutdown¦2 簇间电流差二级告警¦Cluster current difference level 2 alarm¦2 系统预警总¦System pre-warning summary¦2 系统告警总¦System alarm summary¦2 系统故障总¦System fault summary¦2 系统充电禁止¦System charging prohibited¦2 系统放电禁止¦System discharging prohibited¦2 汇流断路器状态反馈¦Bus circuit breaker status feedback¦2 充放电回路异常¦Charge/discharge circuit abnormality¦2 簇间电流差三级告警¦Cluster current difference level 3 alarm¦2
2 | 系统一级报警汇总（严重告警） | U16 |  |  | 4098 | InputRegisters | 1 | AB | 1 | 0 |  | sysL1AlarmSum |  |  | 总电压过压一级报警汇总¦Total voltage overvoltage level 1 alarm summary¦3 总电压欠压一级报警汇总¦Total voltage undervoltage level 1 alarm summary¦3 单体过压一级报警汇总¦Cell overvoltage level 1 alarm summary¦3 单体欠压一级报警汇总¦Cell undervoltage level 1 alarm summary¦3 放电电流过大一级报警汇总¦Discharge overcurrent level 1 alarm summary¦3 充电电流过大一级报警汇总¦Charge overcurrent level 1 alarm summary¦3 放电电池过温一级报警汇总¦Discharge battery overtemperature level 1 alarm summary¦3 放电电池欠温一级报警汇总¦Discharge battery undertemperature level 1 alarm summary¦3 充电电池过温一级报警汇总¦Charge battery overtemperature level 1 alarm summary¦3 充电电池欠温一级报警汇总¦Charge battery undertemperature level 1 alarm summary¦3 绝缘阻值过低一级报警汇总¦Insulation resistance too low level 1 alarm summary¦3 极柱温度过高一级报警汇总¦Pole temperature too high level 1 alarm summary¦3 高压箱连接器温度过高一级报警汇总¦High-voltage box connector overtemperature level 1 alarm summary¦3 单体压差过高一级报警汇总¦Cell voltage difference too high level 1 alarm summary¦3 单体温差过高一级报警汇总¦Cell temperature difference too high level 1 alarm summary¦3 SOC低一级报警汇总¦SOC low level 1 alarm summary¦3
3 | 系统二级报警汇总 | U16 |  |  | 4099 | InputRegisters | 1 | AB | 1 | 0 |  | sysL2AlarmSum |  |  | 总电压过压二级报警汇总¦Total voltage overvoltage level 2 alarm summary¦2 总电压欠压二级报警汇总¦Total voltage undervoltage level 2 alarm summary¦2 单体过压二级报警汇总¦Cell overvoltage level 2 alarm summary¦2 单体欠压二级报警汇总¦Cell undervoltage level 2 alarm summary¦2 放电电流过大二级报警汇总¦Discharge overcurrent level 2 alarm summary¦2 充电电流过大二级报警汇总¦Charge overcurrent level 2 alarm summary¦2 放电电池过温二级报警汇总¦Discharge battery overtemperature level 2 alarm summary¦2 放电电池欠温二级报警汇总¦Discharge battery undertemperature level 2 alarm summary¦2 充电电池过温二级报警汇总¦Charge battery overtemperature level 2 alarm summary¦2 充电电池欠温二级报警汇总¦Charge battery undertemperature level 2 alarm summary¦2 绝缘阻值过低二级报警汇总¦Insulation resistance too low level 2 alarm summary¦2 极柱温度过高二级报警汇总¦Pole temperature too high level 2 alarm summary¦2 高压箱连接器温度过高二级报警汇总¦High-voltage box connector overtemperature level 2 alarm summary¦2 单体压差过高二级报警汇总¦Cell voltage difference too high level 2 alarm summary¦2 单体温差过高二级报警汇总¦Cell temperature difference too high level 2 alarm summary¦2 SOC过低二级报警汇总¦SOC too low level 2 alarm summary¦2
4 | 系统三级报警汇总（预警） | U16 |  |  | 4100 | InputRegisters | 1 | AB | 1 | 0 |  | sysL3AlarmSum |  |  | 总电压过压三级报警汇总¦Total voltage overvoltage level 3 alarm summary¦1 总电压欠压三级报警汇总¦Total voltage undervoltage level 3 alarm summary¦1 单体过压三级报警汇总¦Cell overvoltage level 3 alarm summary¦1 单体欠压三级报警汇总¦Cell undervoltage level 3 alarm summary¦1 放电电流过大三级报警汇总¦Discharge overcurrent level 3 alarm summary¦1 充电电流过大三级报警汇总¦Charge overcurrent level 3 alarm summary¦1 放电电池过温三级报警汇总¦Discharge battery overtemperature level 3 alarm summary¦1 放电电池欠温三级报警汇总¦Discharge battery undertemperature level 3 alarm summary¦1 充电电池过温三级报警汇总¦Charge battery overtemperature level 3 alarm summary¦1 充电电池欠温三级报警汇总¦Charge battery undertemperature level 3 alarm summary¦1 绝缘阻值过低三级报警汇总¦Insulation resistance too low level 3 alarm summary¦1 极柱温度过高三级报警汇总¦Pole temperature too high level 3 alarm summary¦1 高压箱连接器温度过高三级报警汇总¦High-voltage box connector overtemperature level 3 alarm summary¦1 单体压差过高三级报警汇总¦Cell voltage difference too high level 3 alarm summary¦1 单体温差过高三级报警汇总¦Cell temperature difference too high level 3 alarm summary¦1 SOC过低三级报警汇总¦SOC too low level 3 alarm summary¦1
5 | 主控对外一级报警汇总II（严重告警） | U16 |  |  | 4101 | InputRegisters | 1 | AB | 1 | 0 |  | mcExtL1AlarmSumII |  |  | 总压压差过高¦Total voltage difference too high¦3 模组过压¦Module overvoltage¦3 模组欠压¦Module undervoltage¦3 温升过高¦Temperature rise too high¦3 模组压差过大¦Module voltage difference too large¦3 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
6 | 主控对外二级报警汇总II | U16 |  |  | 4102 | InputRegisters | 1 | AB | 1 | 0 |  | mcExtL2AlarmSumII |  |  | 总压压差过高¦Total voltage difference too high¦2 模组过压¦Module overvoltage¦2 模组欠压¦Module undervoltage¦2 温升过高¦Temperature rise too high¦2 模组压差过大¦Module voltage difference too large¦2 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
7 | 主控对外三级报警汇总II（预警） | U16 |  |  | 4103 | InputRegisters | 1 | AB | 1 | 0 |  | mcExtL3AlarmSumII |  |  | 总压压差过高¦Total voltage difference too high¦1 模组过压¦Module overvoltage¦1 模组欠压¦Module undervoltage¦1 温升过高¦Temperature rise too high¦1 模组压差过大¦Module voltage difference too large¦1 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
8 | 主控通信故障报警 | U16 |  |  | 4104 | InputRegisters | 1 | AB | 1 | 0 |  | mcCommFaultAlarm |  |  | 主控1通讯故障¦Master controller 1 communication fault¦2 主控2通讯故障¦Master controller 2 communication fault¦2 主控3通讯故障¦Master controller 3 communication fault¦2 主控4通讯故障¦Master controller 4 communication fault¦2 主控5通讯故障¦Master controller 5 communication fault¦2 主控6通讯故障¦Master controller 6 communication fault¦2 主控7通讯故障¦Master controller 7 communication fault¦2 主控8通讯故障¦Master controller 8 communication fault¦2 主控9通讯故障¦Master controller 9 communication fault¦2 主控10通讯故障¦Master controller 10 communication fault¦2 主控11通讯故障¦Master controller 11 communication fault¦2 主控12通讯故障¦Master controller 12 communication fault¦2 主控13通讯故障¦Master controller 13 communication fault¦2 主控14通讯故障¦Master controller 14 communication fault¦2 主控15通讯故障¦Master controller 15 communication fault¦2 主控16通讯故障¦Master controller 16 communication fault¦2
9 | 主控通信故障报警2 | U16 |  |  | 4105 | InputRegisters | 1 | AB | 1 | 0 |  | mcCommFaultAlarm2 |  |  | 主控17通讯故障¦Master controller 17 communication fault¦2 主控18通讯故障¦Master controller 18 communication fault¦2 主控19通讯故障¦Master controller 19 communication fault¦2 主控20通讯故障¦Master controller 20 communication fault¦2 主控21通讯故障¦Master controller 21 communication fault¦2 主控22通讯故障¦Master controller 22 communication fault¦2 主控23通讯故障¦Master controller 23 communication fault¦2 主控24通讯故障¦Master controller 24 communication fault¦2 主控25通讯故障¦Master controller 25 communication fault¦2 主控26通讯故障¦Master controller 26 communication fault¦2 主控27通讯故障¦Master controller 27 communication fault¦2 主控28通讯故障¦Master controller 28 communication fault¦2 主控29通讯故障¦Master controller 29 communication fault¦2 主控30通讯故障¦Master controller 30 communication fault¦2 主控31通讯故障¦Master controller 31 communication fault¦2 主控32通讯故障¦Master controller 32 communication fault¦2
10 | Rack 故障汇总 | U16 |  |  | 4108 | InputRegisters | 1 | AB | 1 | 0 |  | rackFaultSum |  |  | BMU自检故障汇总¦BMU self-check fault summary¦2 BCU自检故障汇总¦BCU self-check fault summary¦2 熔断器故障汇总¦Fuse fault summary¦2 接触器粘连故障汇总¦Contactor sticking fault summary¦2 BMU通信故障汇总¦BMU communication fault summary¦2 BAU通信故障汇总¦BAU communication fault summary¦2 电流传感器故障汇总¦Current sensor fault summary¦2 绝缘监测设备故障汇总¦Insulation monitoring device fault summary¦2 隔开开关异常断开汇总¦Disconnect switch abnormal opening summary¦2 NTC故障¦NTC fault¦2 高压箱温度故障¦High-voltage box temperature fault¦2 高压回路故障¦High-voltage circuit fault¦2 功能安全故障¦Functional safety fault¦2 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
11 | Rack 故障汇总 II | U16 |  |  | 4108 | InputRegisters | 1 | AB | 1 | 0 | 0 | rackFaultSumII |  |  | BDU通信故障¦BDU communication fault¦2 电操闭合故障¦Electric operation closing fault¦2 电操断开故障¦Electric operation opening fault¦2 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
12 | BAU软件版本号 | U16 |  |  | 4112 | InputRegisters | 1 | AB | 1 | 0 |  | bauSwVerNo
13 | 主版本号 | U16 |  |  | 4113 | InputRegisters | 1 | AB | 1 | 0 |  | majorVerNo
14 | 子版本号 | U16 |  |  | 4114 | InputRegisters | 1 | AB | 1 | 0 |  | minorVerNo
15 | 修正版本号 | U16 |  |  | 4115 | InputRegisters | 1 | AB | 1 | 0 |  | patchVerNo
16 | 协议版本号 | U16 |  |  | 4116 | InputRegisters | 1 | AB | 1 | 0 |  | protoVerNo
17 | 一键并网开关状态 | U16 |  |  | 4136 | InputRegisters | 1 | AB | 1 | 0 |  | oneKeyGridConnSwSts
18 | Rack启用/停用状态高16位 | U16 |  |  | 4137 | InputRegisters | 1 | AB | 1 | 0 |  | rackEnDisStsHi16
19 | Rack启用/停用状态低16位 | U16 |  |  | 4138 | InputRegisters | 1 | AB | 1 | 0 |  | rackEnDisStsLo16
20 | RACK 在线状态高16位 | U16 |  |  | 4141 | InputRegisters | 1 | AB | 1 | 0 |  | rackOnlineStsHi16
21 | RACK 在线状态低16位 | U16 |  |  | 4142 | InputRegisters | 1 | AB | 1 | 0 |  | rackOnlineStsLo16
22 | 系统运行状态 | U16 |  |  | 4145 | InputRegisters | 1 | AB | 1 | 0 |  | sysRunSts
23 | 系统充放电状态 | U16 |  |  | 4146 | InputRegisters | 1 | AB | 1 | 0 |  | sysChgDischgSts
24 | BAU输出干接点状态 | U16 |  |  | 4147 | InputRegisters | 1 | AB | 1 | 0 |  | bauOutDryContactSts
25 | BMS心跳 | U16 |  |  | 4148 | InputRegisters | 1 | AB | 1 | 0 |  | bmsHeartbeat
26 | 分配ID状态 | U16 |  |  | 4149 | InputRegisters | 1 | AB | 1 | 0 |  | idAssignSts
27 | Rack切入失败原因 | U16 |  | Bit0：总压差超限（0:正常, 1:警告；） Bit1：允许切入超时;（0:正常, 1:警告；） | 4150 | InputRegisters | 64 | AB | 1 | 0 |  | rackCutInFailRsn
28 | Rack未启动切入原因 | U16 |  | Bit0:总压压差超限（0:正常, 1:警告；） Bit1:Type1报警未全部解除（0:正常, 1:警告；） Bit2：绝缘报警未解除（0:正常, 1:警告；） Bit3:不满足单体电压过高切出后的切入条件（0:正常, 1:警告；） Bit4:不满足单体过低切出后的切入条件（0:正常, 1:警告；） Bit5:CriticalAlarm未全解除（0:正常, 1:警告；） | 4214 | InputRegisters | 64 | AB | 1 | 0 |  | rackNotStartCutInRsn
29 | 对外复归告警汇总1 | U16 |  |  | 4281 | InputRegisters | 1 | AB | 1 | 0 |  | extResetAlarmSum1 |  |  | 总压过压复归¦Total voltage overvoltage reset¦2 总压欠压复归¦Total voltage undervoltage reset¦2 单体过压复归¦Cell overvoltage reset¦2 单体欠压复归¦Cell undervoltage reset¦2 放电过流复归¦Discharge overcurrent reset¦2 充电过流复归¦Charge overcurrent reset¦2 放电过温复归¦Discharge overtemperature reset¦2 放电欠温复归¦Discharge undertemperature reset¦2 充电过温复归¦Charge overtemperature reset¦2 充电欠温复归¦Charge undertemperature reset¦2 绝缘过低复归¦Insulation too low reset¦2 极柱过温复归¦Pole overtemperature reset¦2 高压箱过温复归¦High-voltage box overtemperature reset¦2 单体压差复归¦Cell voltage difference reset¦2 单体温差复归¦Cell temperature difference reset¦2 预留¦Reserved¦0
30 | 对外复归告警汇总2 | U16 |  |  | 4282 | InputRegisters | 1 | AB | 1 | 0 |  | extResetAlarmSum2 |  |  | 总压压差过高复归¦Total voltage difference too high reset¦2 模组过压复归¦Module overvoltage reset¦2 模组欠压复归¦Module undervoltage reset¦2 温升过高¦Temperature rise too high¦2 模组压差过大¦Module voltage difference too large¦2 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
31 | 总控自身的对外复归告警 | U16 |  |  | 4283 | InputRegisters | 1 | AB | 1 | 0 |  | tcSelfExtResetAlarm |  |  | 簇间电流差过大复归¦Cluster current difference too large reset¦2 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
32 | 对外BAU三级报警（预警） | U16 |  |  | 4284 | InputRegisters | 1 | AB | 1 | 0 |  | extBauL3Alarm |  |  | 簇间电流差预警¦Cluster current difference pre-warning¦1 簇间压差差预警¦Cluster pressure difference pre-warning¦1 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
33 | 对外BAU二级报警 | U16 |  |  | 4285 | InputRegisters | 1 | AB | 1 | 0 |  | extBauL2Alarm |  |  | 簇间电流差告警¦Cluster current difference alarm¦2 簇间压差差告警¦Cluster pressure difference alarm¦2 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
34 | 对外BAU一级报警（严重告警） | U16 |  |  | 4286 | InputRegisters | 1 | AB | 1 | 0 |  | extBauL1Alarm |  |  | 簇间电流差保护¦Cluster current difference protection¦3 簇间压差差保护¦Cluster pressure difference protection¦3 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
50 | 系统总电压 | I16 | V |  | 8193 | InputRegisters | 1 | AB | 0.1 | 0 |  | sysTotalVolt
51 | 系统总电流 | I32 | A |  | 8194 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | sysTotalCurr
52 | 系统SOC | U16 | ‰ |  | 8196 | InputRegisters | 1 | AB | 1 | 0 |  | sysSoc
53 | 系统SOH | U16 | ‰ |  | 8197 | InputRegisters | 1 | AB | 1 | 0 |  | sysSoh
54 | 系统绝缘值 | U16 | KΩ |  | 8198 | InputRegisters | 1 | AB | 1 | 0 |  | sysInsulVal
55 | 系统可充电量 | U16 | kwh |  | 8199 | InputRegisters | 1 | AB | 1 | 0 |  | sysChargeableCap
56 | 系统可放电量 | U16 | kwh |  | 8200 | InputRegisters | 1 | AB | 1 | 0 |  | sysDischargeableCap
57 | 系统允许最大充电电流 | U16 | A |  | 8201 | InputRegisters | 1 | AB | 0.1 | 0 |  | sysMaxAllowChgCurr
58 | 系统允许最大放电电流 | U16 | A |  | 8202 | InputRegisters | 1 | AB | 0.1 | 0 |  | sysMaxAllowDischgCurr
59 | 簇间电流差异值 | U16 | A |  | 8203 | InputRegisters | 1 | AB | 0.1 | 0 |  | interClustCurrDiffVal
60 | 簇间总压差异值 | U16 | v |  | 8204 | InputRegisters | 1 | AB | 0.1 | 0 |  | interClustTotalVoltDiffVal
61 | 系统最高电压电池所在Rack号 | U16 |  |  | 8205 | InputRegisters | 1 | AB | 1 | 0 |  | sysHiVoltBatRackNo
62 | 系统最高电压电池所在组 | U16 |  |  | 8206 | InputRegisters | 1 | AB | 1 | 0 |  | sysHiVoltBatGrp
63 | 系统最高电压电池所在位置 | U16 |  |  | 8207 | InputRegisters | 1 | AB | 1 | 0 |  | sysHiVoltBatPos
64 | 系统最高电池电压 | I16 | mv |  | 8208 | InputRegisters | 1 | AB | 1 | 0 |  | sysHiBatVolt
65 | 系统最低电压电池所在Rack号 | U16 |  |  | 8209 | InputRegisters | 1 | AB | 1 | 0 |  | sysLoVoltBatRackNo
66 | 系统最低电压电池所在组 | U16 |  |  | 8210 | InputRegisters | 1 | AB | 1 | 0 |  | sysLoVoltBatGrp
67 | 系统最低电压电池所在位置 | U16 |  |  | 8211 | InputRegisters | 1 | AB | 1 | 0 |  | sysLoVoltBatPos
68 | 系统最低电池电压 | I16 | mv |  | 8212 | InputRegisters | 1 | AB | 1 | 0 |  | sysLoBatVolt
69 | 系统平均电压 | I16 | mv |  | 8213 | InputRegisters | 1 | AB | 1 | 0 |  | sysAvgVolt
70 | 系统最高温度电池所在Rack号 | U16 |  |  | 8214 | InputRegisters | 1 | AB | 1 | 0 |  | sysHiTempBatRackNo
71 | 系统最高温度电池所在组 | U16 |  |  | 8215 | InputRegisters | 1 | AB | 1 | 0 |  | sysHiTempBatGrp
72 | 系统最高温度电池所在位置 | U16 |  |  | 8216 | InputRegisters | 1 | AB | 1 | 0 |  | sysHiTempBatPos
73 | 系统最高电池温度 | I16 | ℃ |  | 8217 | InputRegisters | 1 | AB | 0.1 | 0 |  | sysHiBatTemp
74 | 系统最低温度电池所在Rack号 | U16 |  |  | 8218 | InputRegisters | 1 | AB | 1 | 0 |  | sysLoTempBatRackNo
75 | 系统最低温度电池所在组 | U16 |  |  | 8219 | InputRegisters | 1 | AB | 1 | 0 |  | sysLoTempBatGrp
76 | 系统最低温度电池所在位置 | U16 |  |  | 8220 | InputRegisters | 1 | AB | 1 | 0 |  | sysLoTempBatPos
77 | 系统最低电池温度 | I16 | ℃ |  | 8221 | InputRegisters | 1 | AB | 0.1 | 0 |  | sysLoBatTemp
78 | 系统平均温度 | I16 | ℃ |  | 8222 | InputRegisters | 1 | AB | 0.1 | 0 |  | sysAvgTemp
79 | 累计充电电量 | U32 | kWh |  | 8223 | InputRegisters | 2 | ABCD | 1 | 0 |  | cumChgEnergy
80 | 累计放电电量 | U32 | kWh |  | 8225 | InputRegisters | 2 | ABCD | 1 | 0 |  | cumDischgEnergy
81 | 当前在网簇数 | U16 |  |  | 8227 | InputRegisters | 1 | AB | 1 | 0 |  | curOnlineClustCnt
82 | 堆内总簇数 | U16 |  |  | 8228 | InputRegisters | 1 | AB | 1 | 0 |  | totalClustCntInStack
83 | 最小并机簇数 | U16 |  |  | 8229 | InputRegisters | 1 | AB | 1 | 0 |  | minParallelClustCnt
84 | 堆可用放电功率 | U16 | kw |  | 8230 | InputRegisters | 1 | AB | 1 | 0 |  | stackAvailDischgPwr
85 | 堆可用充电功率 | U16 | kw |  | 8231 | InputRegisters | 1 | AB | 1 | 0 |  | stackAvailChgPwr
100 | 总控IO告警 | U16 |  |  | 1536 | InputRegisters | 1 | AB | 1 | 0 |  | tcIoAlarm |  |  | 急停报警¦Emergency stop alarm¦3 消防预警反馈报警¦Fire pre-warning feedback alarm¦2 消防火警反馈报警¦Fire alarm feedback alarm¦3 直流SPD报警¦DC SPD alarm¦2 交流SPD报警¦AC SPD alarm¦2 门禁报警¦Access control alarm¦1 防爆风机状态报警¦Explosion-proof fan status alarm¦1 防爆风机状态预警¦Explosion-proof fan status pre-warning¦1 防爆风机故障报警¦Explosion-proof fan fault alarm¦1 UPS交流失电报警¦UPS AC power loss alarm¦1 UPS直流失电报警¦UPS DC power loss alarm¦1 UPS故障报警¦UPS fault alarm¦1 液冷机组故障报警¦Liquid cooling unit fault alarm¦2 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
101 | 设备通讯告警 | U16 |  |  | 1537 | InputRegisters | 1 | AB | 1 | 0 |  | devCommAlarm |  |  | 温湿度传感器通讯丢失¦Temperature and humidity sensor communication loss¦1 电表通讯丢失¦Electric meter communication loss¦1 空调通讯丢失¦Air conditioner communication loss¦2 液冷通讯丢失¦Liquid cooling communication loss¦2 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0 预留¦Reserved¦0
102 | 温湿度传感器1的温度值 | U16 |  |  | 1538 | InputRegisters | 1 | AB | 0.1 | 0 |  | tempHumidSens1TempVal
103 | 温湿度传感器1的湿度值 | U16 |  |  | 1539 | InputRegisters | 1 | AB | 0.1 | 0 |  | tempHumidSens1HumidVal
104 | 空调1整机运行状态 | U16 |  |  | 1540 | InputRegisters | 1 | AB | 1 | 0 |  | ac1OverallRunSts
105 | 空调1室内温度 | U16 |  |  | 1541 | InputRegisters | 1 | AB | 0.1 | 0 |  | ac1IndoorTemp
106 | 液冷1出水温度 | U16 |  |  | 1542 | InputRegisters | 1 | AB | 1 | 0 |  | liqCool1OutletWaterTemp
107 | 液冷1回水温度 | U16 |  |  | 1543 | InputRegisters | 1 | AB | 1 | 0 |  | liqCool1ReturnWaterTemp
108 | 液冷1环境温度 | U16 |  |  | 1544 | InputRegisters | 1 | AB | 1 | 0 |  | liqCool1AmbientTemp

## 遥信
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位

## 遥调
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位
2000 | Bank静态簇间压差过高触发阈值 | U16 | V |  | 20481 | HoldingRegisters | 1 | AB | 0.1 | 0 | 214 | bankStaticInterClustVoltDiffHiTrigThr
2001 | Bank静态簇间压差过高恢复阈值 | U16 | V |  | 20482 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankStaticInterClustVoltDiffHiRecThr
2002 | Bank动态簇间压差过高触发阈值 | U16 | V |  | 20483 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankDynInterClustVoltDiffHiTrigThr
2003 | Bank动态簇间压差过高恢复阈值 | U16 | V |  | 20484 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankDynInterClustVoltDiffHiRecThr
2004 | Bank簇间电流差过高三级触发阈值（预警） | U16 | A |  | 20485 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankInterClustCurrDiffHiL3TrigThr
2005 | Bank簇间电流差过高三级恢复阈值（预警） | U16 | A |  | 20486 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankInterClustCurrDiffHiL3RecThr
2006 | Bank簇间电流差过高二级触发阈值 | U16 | A |  | 20487 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankInterClustCurrDiffHiL2TrigThr
2007 | Bank簇间电流差过高二级恢复阈值 | U16 | A |  | 20488 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankInterClustCurrDiffHiL2RecThr
2008 | Bank簇间电流差过高一级触发阈值（严重告警） | U16 | A |  | 20489 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankInterClustCurrDiffHiL1TrigThr
2009 | Bank簇间电流差过高一级恢复阈值（严重告警） | U16 | A |  | 20490 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankInterClustCurrDiffHiL1RecThr
2010 | Bank动态簇间压差过高告警触发阈值 | U16 | V |  | 20491 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankDynInterClustVoltDiffHiAlarmTrigThr
2011 | Bank动态簇间压差过高保护触发阈值 | U16 | V |  | 20492 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankDynInterClustVoltDiffHiProtTrigThr
2012 | Bank静态簇间压差过高告警触发阈值 | U16 | V |  | 20493 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankStaticInterClustVoltDiffHiAlarmTrigThr
2013 | Bank静态簇间压差过高保护触发阈值 | U16 | V |  | 20494 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankStaticInterClustVoltDiffHiProtTrigThr
2014 | Bank动态簇间压差过高告警恢复阈值 | U16 | V |  | 20495 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankDynInterClustVoltDiffHiAlarmRecThr
2015 | Bank动态簇间压差过高保护恢复阈值 | U16 | V |  | 20496 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankDynInterClustVoltDiffHiProtRecThr
2016 | Bank静态簇间压差过高告警恢复阈值 | U16 | V |  | 20497 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankStaticInterClustVoltDiffHiAlarmRecThr
2017 | Bank静态簇间压差过高保护恢复阈值 | U16 | V |  | 20498 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | bankStaticInterClustVoltDiffHiProtRecThr
2018 | 预留 | U16 |  |  | 20499 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | reserved
2019 | BAU本地IP地址（网口1） | U16 |  |  | 20992 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauLocalIpAddrPort1
2020 | BAU本地IP地址（网口1） | U16 |  |  | 20993 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauLocalIpAddrPort1
2021 | BAU本地IP地址（网口1） | U16 |  |  | 20994 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauLocalIpAddrPort1
2022 | BAU本地IP地址（网口1） | U16 |  |  | 20995 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauLocalIpAddrPort1
2023 | 网关IP地址（网口1） | U16 |  |  | 20996 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | gatewayIpAddrPort1
2024 | 网关IP地址（网口1） | U16 |  |  | 20997 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | gatewayIpAddrPort1
2025 | 网关IP地址（网口1） | U16 |  |  | 20998 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | gatewayIpAddrPort1
2026 | 网关IP地址（网口1） | U16 |  |  | 20999 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | gatewayIpAddrPort1
2027 | 子网掩码（网口1） | U16 |  |  | 21000 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | subnetMaskPort1
2028 | 子网掩码（网口1） | U16 |  |  | 21001 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | subnetMaskPort1
2029 | 子网掩码（网口1） | U16 |  |  | 21002 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | subnetMaskPort1
2030 | 子网掩码（网口1） | U16 |  |  | 21003 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | subnetMaskPort1
2031 | 客户端1本地端口号（网口1） | U16 |  |  | 21004 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client1LocalPortNoPort1
2032 | 客户端2本地端口号（网口1） | U16 |  |  | 21005 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client2LocalPortNoPort1
2033 | 客户端3本地端口号（网口1） | U16 |  |  | 21006 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client3LocalPortNoPort1
2034 | 客户端4本地端口号（网口1） | U16 |  |  | 21007 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client4LocalPortNoPort1
2035 | 客户端5本地端口号（网口1） | U16 |  |  | 21008 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client5LocalPortNoPort1
2036 | 客户端6本地端口号（网口1） | U16 |  |  | 21009 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client6LocalPortNoPort1
2037 | 客户端7本地端口号（网口1） | U16 |  |  | 21010 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client7LocalPortNoPort1
2038 | 客户端8本地端口号（网口1） | U16 |  |  | 21011 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client8LocalPortNoPort1
2039 | BAU本地IP地址（网口2） | U16 |  |  | 21012 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauLocalIpAddrPort2
2040 | BAU本地IP地址（网口2） | U16 |  |  | 21013 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauLocalIpAddrPort2
2041 | BAU本地IP地址（网口2） | U16 |  |  | 21014 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauLocalIpAddrPort2
2042 | BAU本地IP地址（网口2） | U16 |  |  | 21015 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauLocalIpAddrPort2
2043 | 网关IP地址（网口2） | U16 |  |  | 21016 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | gatewayIpAddrPort2
2044 | 网关IP地址（网口2） | U16 |  |  | 21017 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | gatewayIpAddrPort2
2045 | 网关IP地址（网口2） | U16 |  |  | 21018 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | gatewayIpAddrPort2
2046 | 网关IP地址（网口2） | U16 |  |  | 21019 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | gatewayIpAddrPort2
2047 | 子网掩码（网口2） | U16 |  |  | 21020 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | subnetMaskPort2
2048 | 子网掩码（网口2） | U16 |  |  | 21021 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | subnetMaskPort2
2049 | 预留 | U16 |  |  | 21022 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | reserved
2050 | 子网掩码（网口2） | U16 |  |  | 21023 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | subnetMaskPort2
2051 | 子网掩码（网口2） | U16 |  |  | 21024 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | subnetMaskPort2
2052 | 客户端1本地端口号（网口2） | U16 |  |  | 21025 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client1LocalPortNoPort2
2053 | 客户端2本地端口号（网口2） | U16 |  |  | 21026 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client2LocalPortNoPort2
2054 | 客户端3本地端口号（网口2） | U16 |  |  | 21027 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client3LocalPortNoPort2
2055 | 客户端4本地端口号（网口2） | U16 |  |  | 21028 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client4LocalPortNoPort2
2056 | 客户端5本地端口号（网口2） | U16 |  |  | 21029 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client5LocalPortNoPort2
2057 | 客户端6本地端口号（网口2） | U16 |  |  | 21030 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client6LocalPortNoPort2
2058 | 客户端7本地端口号（网口2） | U16 |  |  | 21031 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client7LocalPortNoPort2
2059 | 客户端8本地端口号（网口2） | U16 |  |  | 21032 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | client8LocalPortNoPort2
2060 | 年 | U16 |  |  | 21033 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | year
2061 | 日 | U16 |  |  | 21034 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | day
2062 | 分 | U16 |  |  | 21035 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | minute
2063 | 毫秒 | U16 |  |  | 21036 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | millisecond
2064 | NTP时区 | U16 |  |  | 21037 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | ntpTimeZone
2065 | 年 | U16 |  |  | 21038 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | year
2066 | 月 | U16 |  |  | 21039 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | month
2067 | 日 | U16 |  |  | 21040 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | day
2068 | 时 | U16 |  |  | 21041 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | hour
2069 | 分 | U16 |  |  | 21042 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | minute
2070 | 秒 | U16 |  |  | 21043 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | second
2071 | BAU-EMS 通讯故障（心跳） | U16 |  |  | 21044 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | bauEmsCommFaultHeartbeat

## 遥控
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位 | 重复次数 | 地址步长 | 告警等级
3000 | 一键并网开关 | bool |  |  | 12289 | Coils | 1 | AB | 1 | 0 |  | oneKeyGridConnSwitch
3001 | 复位BAU | bool |  |  | 12290 | Coils | 1 | AB | 1 | 0 |  | resetBau
3002 | 绝缘采样功能开关 | bool |  |  | 12291 | Coils | 1 | AB | 1 | 0 |  | insulSamplingFuncSwitch
3003 | 清除PCS控制失效 | bool |  |  | 12292 | Coils | 1 | AB | 1 | 0 |  | clearPcsCtrlFailure
3004 | 设置Rack {n} 启用/停用 | bool |  |  | 12293 | Coils | 1 | AB | 1 | 0 |  | setRack{n}EnDis |  |  |  | 64 | 1
3069 | 本地/远程控制切换 | bool |  | 0：本地+远程均使能 1：本地 2：远程 | 12357 | Coils | 1 | AB | 1 | 0 |  | localRemoteCtrlSwitch
3070 | 重置主控ID | bool |  | 0x0:初始化，0x1启动ID自动分配，0x2分配成功，0x3分配失败 | 12358 | Coils | 1 | AB | 1 | 0 |  | resetMainCtrlId
3071 | 一键复归 | bool |  | 1：复归 | 12359 | Coils | 1 | AB | 1 | 0 |  | oneKeyReset
3072 | 电操控制 | u8 |  | 1：闭合电操 2：断开电操 3：电操脱扣 | 12360 | Coils | 1 | AB | 1 | 0 |  | motorOperatedCtrl