## 遥测
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位
1 | 环境温度 | I16 | ℃ |  | 1 | InputRegisters | 1 | AB | 0.1 | 0 |  | ambientTemperature | {"en":"ambient temperature"}
2 | 回液温度 | I16 | ℃ |  | 2 | InputRegisters | 1 | AB | 0.1 | 0 |  | returnLiquidTemperature | {"en":"Return liquid temperature"}
3 | 供液温度 | I16 | ℃ |  | 3 | InputRegisters | 1 | AB | 0.1 | 0 |  | liquidSupplyTemperature | {"en":"Liquid supply temperature"}
4 | 回液压力 | I16 | kPa |  | 4 | InputRegisters | 1 | AB | 1 | 0 |  | returnFluidPressure | {"en":"Return fluid pressure"}
5 | 供液压力 | I16 | kPa |  | 5 | InputRegisters | 1 | AB | 1 | 0 |  | liquidSupplyPressure | {"en":"liquid supply pressure"}
6 | 系统1风机挡位 | U16 |  | 共45挡，0挡表示停止，1挡为最低转速，45挡为最高转速 | 17 | InputRegisters | 1 | AB | 1 | 0 |  | system1FanGear | {"en":"System 1 fan gear"}
7 | 系统1第一组风机转速 | U16 | %/rps | EC风机为目标转速（%），AC风机为反馈转速（rps） | 18 | InputRegisters | 1 | AB | 1 | 0 |  | system1FirstGroupFanSpeed | {"en":"System 1 first group fan speed"}
8 | 系统1第二组风机转速 | U16 | %/rps |  | 19 | InputRegisters | 1 | AB | 1 | 0 |  | system1SecondGroupFanSpeed | {"en":"System 1 second group fan speed"}
9 | 系统1第三组风机转速/系统1风机电流 | U16 | %或A | EC风机为目标转速（%），AC风机为电流（A） | 20 | InputRegisters | 1 | AB | 1 | 0 |  | system1ThirdGroupFanSpeedSystem1FanCurrent | {"en":"System 1 third group fan speed/System 1 fan current"}
10 | 系统1压缩机状态 | U16 |  |  | 21 | InputRegisters | 1 | AB | 1 | 0 |  | system1CompressorStatus | {"en":"System 1 Compressor Status"} | 0 关机¦Shutdown 1 启动运行（平台1）¦Startup (Platform 1) 2 启动运行（平台2）¦Startup (Platform 2) 3 启动运行（平台3）¦Startup (Platform 3) 4 启动运行（平台4）¦Startup (Platform 4) 5 升频¦Speed Increase 6 降频¦Speed Decrease 7 正常运行（非启动阶段）¦Normal Operation (Non-Startup Phase)
11 | 系统1压缩机目标频率 | U16 | Hz |  | 22 | InputRegisters | 1 | AB | 1 | 0 |  | system1CompressorTargetFrequency | {"en":"System 1 Compressor Target Frequency"}
12 | 系统1压缩机运行频率 | U16 | Hz |  | 23 | InputRegisters | 1 | AB | 1 | 0 |  | system1CompressorOperatingFrequency | {"en":"System 1 Compressor Operating Frequency"}
13 | 系统1电子膨胀阀开度 | U16 |  |  | 28 | InputRegisters | 1 | AB | 1 | 0 |  | system1ElectronicExpansionValveOpening | {"en":"System 1 Electronic Expansion Valve Opening"}
14 | 系统2压缩机状态 | U16 |  |  | 37 | InputRegisters | 1 | AB | 1 | 0 |  | system2CompressorStatus | {"en":"System 2 Compressor Status"} | 0 关机¦Shutdown 1 启动运行（平台1）¦Startup (Platform 1) 2 启动运行（平台2）¦Startup (Platform 2) 3 启动运行（平台3）¦Startup (Platform 3) 4 启动运行（平台4）¦Startup (Platform 4) 5 升频¦Speed Increase 6 降频¦Speed Decrease 7 正常运行（非启动阶段）¦Normal Operation (Non-Startup Phase)
15 | 系统2压缩机目标频率 | U16 | Hz |  | 38 | InputRegisters | 1 | AB | 1 | 0 |  | targetFrequencyOfSystem2Compressor | {"en":"Target frequency of system 2 compressor"}
16 | 系统2压缩机运行频率 | U16 | Hz |  | 39 | InputRegisters | 1 | AB | 1 | 0 |  | system2CompressorOperatingFrequency | {"en":"System 2 Compressor Operating Frequency"}
17 | 系统2电子膨胀阀开度 | U16 |  |  | 44 | InputRegisters | 1 | AB | 1 | 0 |  | system2ElectronicExpansionValveOpening | {"en":"System 2 Electronic Expansion Valve Opening"}
18 | 机组运行模式 | U16 |  |  | 45 | InputRegisters | 1 | AB | 1 | 0 |  | unitOperationMode | {"en":"Unit operation mode"} | 0 待机¦StandBy 1 制冷¦Cooling 2 制热Heating 3 自循环¦SelfCycle
19 | 水泵目标转速 | U16 | % |  | 46 | InputRegisters | 1 | AB | 1 | 0 |  | targetSpeedOfWaterPump | {"en":"Target speed of water pump"}
20 | 故障代码1 | U16 |  |  | 59 | InputRegisters | 1 | AB | 1 | 0 |  | faultCode1 | {"en":"Fault code 1"} |  | 环境温度传感器故障¦Ambient temperature sensor fault¦2 回水温度传感器故障¦Return water temperature sensor fault¦2 出水温度传感器故障¦Outlet water temperature sensor fault¦2 预留¦Reserved¦0 回水压力传感器故障¦Return water pressure sensor fault¦2 出水压力传感器故障¦Outlet water pressure sensor fault¦2 吸气温度1传感器故障¦Suction temperature 1 sensor fault¦2 排气温度1传感器故障¦Discharge temperature 1 sensor fault¦2 吸气压力1传感器故障¦Suction pressure 1 sensor fault¦2 排气压力1传感器故障¦Discharge pressure 1 sensor fault¦2 吸气温度2传感器故障¦Suction temperature 2 sensor fault¦2 排气温度2传感器故障¦Discharge temperature 2 sensor fault¦2 吸气压力2传感器故障¦Suction pressure 2 sensor fault¦2 排气压力2传感器故障¦Discharge pressure 2 sensor fault¦2 系统1高压告警（开关）¦System 1 high pressure alarm (switch)¦2 系统2高压告警（开关）¦System 2 high pressure alarm (switch)¦2
21 | 故障代码2 | U16 |  |  | 60 | InputRegisters | 1 | AB | 1 | 0 |  | faultCode2 | {"en":"Fault code 2"} |  | 环温超限¦Ambient temperature over limit¦2 水泵故障¦Water pump fault¦2 系统1排气过热度过低¦System 1 discharge superheat too low¦2 系统2排气过热度过低¦System 2 discharge superheat too low¦2 系统1吸气压力低¦System 1 suction pressure low¦2 系统2吸气压力低¦System 2 suction pressure low¦2 系统1排气压力过高¦System 1 discharge pressure too high¦2 系统2排气压力过高¦System 2 discharge pressure too high¦2 系统1排气温度过高¦System 1 discharge temperature too high¦2 系统2排气温度过高¦System 2 discharge temperature too high¦2 系统1压比过高¦System 1 pressure ratio too high¦2 系统2压比过高¦System 2 pressure ratio too high¦2 系统1压比过低¦System 1 pressure ratio too low¦2 系统2压比过低¦System 2 pressure ratio too low¦2 系统1泄露故障¦System 1 refrigerant leakage fault¦2 系统2泄露故障¦System 2 refrigerant leakage fault¦2
22 | 故障代码3 | U16 |  |  | 61 | InputRegisters | 1 | AB | 1 | 0 |  | faultCode3 | {"en":"Fault code 3"} |  | 压缩机1过流保护¦Compressor 1 overcurrent protection¦2 压缩机2过流保护¦Compressor 2 overcurrent protection¦2 压缩机1驱动过温保护¦Compressor 1 drive over-temperature protection¦2 压缩机2驱动过温保护¦Compressor 2 drive over-temperature protection¦2 水泵驱动过流保护¦Water pump drive overcurrent protection¦2 水泵驱动过温保护¦Water pump drive over-temperature protection¦2 出水温度过低保护¦Outlet water temperature too low protection¦2 水压过低保护¦Water pressure too low protection¦2 水压过高保护¦Water pressure too high protection¦2 水温差过高保护¦Water temperature differential too high protection¦2 水压差过小/滤网堵塞¦Water pressure differential too low / filter clogged¦2 水箱液位过低¦Water tank level too low¦2 PTC过载保护¦PTC overload protection¦2 风机1故障¦Fan 1 fault¦2 风机2故障¦Fan 2 fault¦2 风机3故障/风机3驱动故障（系统2）¦Fan 3 fault / Fan 3 drive fault (System 2)¦2
23 | 故障代码4 | U16 |  |  | 62 | InputRegisters | 1 | AB | 1 | 0 |  | faultCode4 | {"en":"Fault code 4"} |  | 风机4驱动故障（系统2）¦Fan 4 drive fault (System 2)¦2 内存（E2）错误¦Memory (E2) error¦2 预留¦Reserved¦0 水泵驱动离线¦Water pump drive offline¦2 压缩机1驱动离线¦Compressor 1 drive offline¦2 压缩机2驱动离线¦Compressor 2 drive offline¦2 压缩机1驱动故障¦Compressor 1 drive fault¦2 压缩机2驱动故障¦Compressor 2 drive fault¦2 风机1驱动离线¦Fan 1 drive offline¦2 风机2驱动离线¦Fan 2 drive offline¦2 风机1驱动故障¦Fan 1 drive fault¦2 风机2驱动故障¦Fan 2 drive fault¦2 上位机离线故障¦Host computer offline fault¦2 水温过高保护¦Water temperature too high protection¦2 风机3驱动离线（系统2）¦Fan 3 drive offline (System 2)¦2 风机4驱动离线（系统2）¦Fan 4 drive offline (System 2)¦2
24 | 故障代码5 | U16 |  |  | 63 | InputRegisters | 1 | AB | 1 | 0 | 0 | faultCode5 | {"en":"Fault code 5"}
25 | 系统2风机挡位 | U16 |  | 共45挡，0挡表示停止，1挡为最低转速，45挡为最高转速 | 69 | InputRegisters | 1 | AB | 1 | 0 |  | system2FanGear | {"en":"System 2 fan gear"}
26 | 系统2第一组风机转速 | U16 | %/rps | EC风机为目标转速（%），AC风机为反馈转速（rps） | 70 | InputRegisters | 1 | AB | 1 | 0 |  | system2FirstGroupFanSpeed | {"en":"System 2 first group fan speed"}
27 | 系统2第二组风机转速 | U16 | %/rps |  | 71 | InputRegisters | 1 | AB | 1 | 0 |  | system2SecondGroupFanSpeed | {"en":"System 2 second group fan speed"}
28 | 系统2第三组风机转速/系统2风机电流 | U16 | %或A | EC风机为目标转速（%），AC风机为电流（A） | 72 | InputRegisters | 1 | AB | 1 | 0 |  | system2ThirdGroupFanSpeedSystem2FanCurrent | {"en":"System 2 third group fan speed/System 2 fan current"}

## 遥调
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位
2000 | 机组开关机使能 | U16 |  |  | 1 | HoldingRegisters | 1 | AB | 1 | 0 |  | unitPowerOnOffEnable | {"en":"Unit power on/off enable"} | 0 关机¦ShutDown 1 启动¦Start
2001 | 机组运行功能选择 | U16 |  |  | 2 | HoldingRegisters | 1 | AB | 1 | 0 |  | unitOperationFunctionSelection | {"en":"Unit operation function selection"} | 0 自动¦Auto 1 制冷¦Cooling 2 制热¦Heating
2002 | 制冷设定出水温度 | U16 | ℃ |  | 3 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | coolingSetWaterOutletTemperature | {"en":"Cooling set water outlet temperature"}
2003 | 制冷设定回水温度 | U16 | ℃ |  | 4 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | refrigerationSetReturnWaterTemperature | {"en":"Refrigeration set return water temperature"}
2004 | 加热设定出水温度 | U16 | ℃ |  | 5 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | heatingSetWaterOutletTemperature | {"en":"Heating set water outlet temperature"}
2005 | 加热设定回水温度 | U16 | ℃ |  | 6 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | heatingSetReturnWaterTemperature | {"en":"Heating set return water temperature"}
2006 | 制冷停止温差 | U16 | ℃ |  | 8 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | coolingStopTemperatureDifference | {"en":"Cooling stop temperature difference"}
2007 | 制冷启动温差 | U16 | ℃ |  | 9 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | temperatureDifferenceDuringRefrigerationStartUp | {"en":"Temperature difference during refrigeration start-up"}
2008 | 加热停止温差 | U16 | ℃ |  | 10 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | heatingStopTemperatureDifference | {"en":"Heating stop temperature difference"}
2009 | 加热启动温差 | U16 | ℃ |  | 11 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | heatingStartUpTemperatureDifference | {"en":"Heating start-up temperature difference"}
2010 | 水温控制选择 | U16 |  |  | 18 | HoldingRegisters | 1 | AB | 1 | 0 |  | waterTemperatureControlSelection | {"en":"Water temperature control selection"}
2011 | 补液泵强制补液 | U16 |  |  | 54 | HoldingRegisters | 1 | AB | 1 | 0 |  | forcedFluidReplacementPump | {"en":"Forced fluid replacement pump"} | 0 禁止¦Disable 1 使能¦Enbale
2012 | RS485从站地址 | U16 |  |  | 55 | HoldingRegisters | 1 | AB | 1 | 0 |  | rs485SlaveAddress | {"en":"RS485 slave address"}