## 遥测
序号 | 名称 | 地址 | 系数 | 偏移 | 单位 | 备注 | 启用 | 键 | 名称翻译
1 | 相电压UA | 16385 | 1 | 0 | V | 400V侧多功能表 |  | phaseVoltageUa | {"en":"Phase voltage UA"}
2 | 相电压UB | 16386 | 1 | 0 | V | 400V侧多功能表 |  | phaseVoltageUb | {"en":"Phase voltage UB"}
3 | 相电压UC | 16387 | 1 | 0 | V | 400V侧多功能表 |  | phaseVoltageUc | {"en":"Phase voltage UC"}
4 | 线电压UAB | 16388 | 1 | 0 | V | 400V侧多功能表 |  | lineVoltageUab | {"en":"Line voltage UAB"}
5 | 线电压UBC | 16389 | 1 | 0 | V | 400V侧多功能表 |  | lineVoltageUbc | {"en":"Line voltage UBC"}
6 | 线电压UCA | 16390 | 1 | 0 | V | 400V侧多功能表 |  | lineVoltageUca | {"en":"Line voltage UCA"}
7 | 相电流IA | 16391 | 1 | 0 | A | 400V侧多功能表 |  | phaseCurrentIa | {"en":"Phase current IA"}
8 | 相电流IB | 16392 | 1 | 0 | A | 400V侧多功能表 |  | phaseCurrentIb | {"en":"Phase current IB"}
9 | 相电流IC | 16393 | 1 | 0 | A | 400V侧多功能表 |  | phaseCurrentIc | {"en":"Phase current IC"}
10 | A相有功功率Pa | 16394 | 1 | 0 | kW | 400V侧多功能表 |  | aPhaseActivePowerPa | {"en":"A-phase active power Pa"}
11 | B相有功功率Pb | 16395 | 1 | 0 | kW | 400V侧多功能表 |  | bPhaseActivePowerPb | {"en":"B-phase active power Pb"}
12 | C相有功功率Pc | 16396 | 1 | 0 | kW | 400V侧多功能表 |  | cPhaseActivePowerPc | {"en":"C-phase active power Pc"}
13 | 总有功功率Ps | 16397 | 1 | 0 | kW | 400V侧多功能表 |  | totalActivePowerPs | {"en":"Total active power Ps"}
14 | A相无功功率Qa | 16398 | 1 | 0 | kVar | 400V侧多功能表 |  | aPhaseReactivePowerQa | {"en":"A-phase reactive power Qa"}
15 | B相无功功率Qb | 16399 | 1 | 0 | kVar | 400V侧多功能表 |  | bPhaseReactivePowerQb | {"en":"B-phase reactive power Qb"}
16 | C相无功功率Qc | 16400 | 1 | 0 | kVar | 400V侧多功能表 |  | cPhaseReactivePowerQc | {"en":"C-phase reactive power Qc"}
17 | 总无功功率Qs | 16401 | 1 | 0 | kVar | 400V侧多功能表 |  | totalReactivePowerQs | {"en":"Total reactive power Qs"}
18 | A相视在功率VAa | 16402 | 1 | 0 | kVa | 400V侧多功能表 |  | aPhaseApparentPowerVaa | {"en":"A-phase apparent power VAa"}
19 | B相视在功率VAb | 16403 | 1 | 0 | kVa | 400V侧多功能表 |  | bPhaseApparentPowerVab | {"en":"B-phase apparent power VAb"}
20 | C相视在功率VAc | 16404 | 1 | 0 | kVa | 400V侧多功能表 |  | cPhaseApparentPowerVac | {"en":"C-phase apparent power VAc"}
21 | 总视在功率VAs | 16405 | 1 | 0 | kVa | 400V侧多功能表 |  | totalApparentPowerVas | {"en":"Total apparent power VAs"}
22 | A相功率因数PFa | 16406 | 1 | 0 |  | 400V侧多功能表 |  | aPhasePowerFactorPfa | {"en":"A-phase power factor PFa"}
23 | B相功率因数PFb | 16407 | 1 | 0 |  | 400V侧多功能表 |  | bPhasePowerFactorPfb | {"en":"B-phase power factor PFb"}
24 | C相功率因数PFc | 16408 | 1 | 0 |  | 400V侧多功能表 |  | cPhasePowerFactorPfc | {"en":"C-phase power factor PFc"}
25 | 总功率因数PFs | 16409 | 1 | 0 |  | 400V侧多功能表 |  | totalPowerFactorPfs | {"en":"Total power factor PFs"}
26 | 频率 | 16410 | 1 | 0 | Hz | 400V侧多功能表 |  | frequency | {"en":"frequency"}
27 | 总有功电度 | 16411 | 1 | 0 | kWh | 400V侧多功能表 |  | totalActiveEnergy | {"en":"Total active energy"}
28 | 正向有功电度 | 16412 | 1 | 0 | kWh | 400V侧多功能表 |  | positiveActiveEnergy | {"en":"Positive active energy"}
29 | 反向有功电度 | 16413 | 1 | 0 | kWh | 400V侧多功能表 |  | reverseActiveEnergy | {"en":"Reverse active energy"}
30 | 总无功电度 | 16414 | 1 | 0 | kVarh | 400V侧多功能表 |  | totalReactivePower | {"en":"Total reactive power"}
31 | 正向无功电度 | 16415 | 1 | 0 | kVarh | 400V侧多功能表 |  | positiveReactivePower | {"en":"Positive reactive power"}
32 | 反向无功电度 | 16416 | 1 | 0 | kVarh | 400V侧多功能表 |  | reverseReactivePower | {"en":"Reverse reactive power"}
33 | 温度1 | 16417 | 1 | 0 | ℃ | AA1柜温湿度控制器 |  | temperature1 | {"en":"Temperature 1"}
34 | 湿度1 | 16418 | 1 | 0 | %RH | AA1柜温湿度控制器 |  | humidity1 | {"en":"Humidity 1"}
35 | 温度2 | 16419 | 1 | 0 | ℃ | AA1柜温湿度控制器 |  | temperature2 | {"en":"Temperature 2"}
36 | 湿度2 | 16420 | 1 | 0 | %RH | AA1柜温湿度控制器 |  | humidity2 | {"en":"Humidity 2"}
37 | 相电压UA | 16421 | 1 | 0 | V | 690V侧1多功能表 |  | phaseVoltageUa | {"en":"Phase voltage UA"}
38 | 相电压UB | 16422 | 1 | 0 | V | 690V侧1多功能表 |  | phaseVoltageUb | {"en":"Phase voltage UB"}
39 | 相电压UC | 16423 | 1 | 0 | V | 690V侧1多功能表 |  | phaseVoltageUc | {"en":"Phase voltage UC"}
40 | 线电压UAB | 16424 | 1 | 0 | V | 690V侧1多功能表 |  | lineVoltageUab | {"en":"Line voltage UAB"}
41 | 线电压UBC | 16425 | 1 | 0 | V | 690V侧1多功能表 |  | lineVoltageUbc | {"en":"Line voltage UBC"}
42 | 线电压UCA | 16426 | 1 | 0 | V | 690V侧1多功能表 |  | lineVoltageUca | {"en":"Line voltage UCA"}
43 | 相电流IA | 16427 | 1 | 0 | A | 690V侧1多功能表 |  | phaseCurrentIa | {"en":"Phase current IA"}
44 | 相电流IB | 16428 | 1 | 0 | A | 690V侧1多功能表 |  | phaseCurrentIb | {"en":"Phase current IB"}
45 | 相电流IC | 16429 | 1 | 0 | A | 690V侧1多功能表 |  | phaseCurrentIc | {"en":"Phase current IC"}
46 | A相有功功率Pa | 16430 | 1 | 0 | kW | 690V侧1多功能表 |  | aPhaseActivePowerPa | {"en":"A-phase active power Pa"}
47 | B相有功功率Pb | 16431 | 1 | 0 | kW | 690V侧1多功能表 |  | bPhaseActivePowerPb | {"en":"B-phase active power Pb"}
48 | C相有功功率Pc | 16432 | 1 | 0 | kW | 690V侧1多功能表 |  | cPhaseActivePowerPc | {"en":"C-phase active power Pc"}
49 | 总有功功率Ps | 16433 | 1 | 0 | kW | 690V侧1多功能表 |  | totalActivePowerPs | {"en":"Total active power Ps"}
50 | A相无功功率Qa | 16434 | 1 | 0 | kVar | 690V侧1多功能表 |  | aPhaseReactivePowerQa | {"en":"A-phase reactive power Qa"}
51 | B相无功功率Qb | 16435 | 1 | 0 | kVar | 690V侧1多功能表 |  | bPhaseReactivePowerQb | {"en":"B-phase reactive power Qb"}
52 | C相无功功率Qc | 16436 | 1 | 0 | kVar | 690V侧1多功能表 |  | cPhaseReactivePowerQc | {"en":"C-phase reactive power Qc"}
53 | 总无功功率Qs | 16437 | 1 | 0 | kVar | 690V侧1多功能表 |  | totalReactivePowerQs | {"en":"Total reactive power Qs"}
54 | A相视在功率VAa | 16438 | 1 | 0 | kVa | 690V侧1多功能表 |  | aPhaseApparentPowerVaa | {"en":"A-phase apparent power VAa"}
55 | B相视在功率VAb | 16439 | 1 | 0 | kVa | 690V侧1多功能表 |  | bPhaseApparentPowerVab | {"en":"B-phase apparent power VAb"}
56 | C相视在功率VAc | 16440 | 1 | 0 | kVa | 690V侧1多功能表 |  | cPhaseApparentPowerVac | {"en":"C-phase apparent power VAc"}
57 | 总视在功率VAs | 16441 | 1 | 0 | kVa | 690V侧1多功能表 |  | totalApparentPowerVas | {"en":"Total apparent power VAs"}
58 | A相功率因数PFa | 16442 | 1 | 0 |  | 690V侧1多功能表 |  | aPhasePowerFactorPfa | {"en":"A-phase power factor PFa"}
59 | B相功率因数PFb | 16443 | 1 | 0 |  | 690V侧1多功能表 |  | bPhasePowerFactorPfb | {"en":"B-phase power factor PFb"}
60 | C相功率因数PFc | 16444 | 1 | 0 |  | 690V侧1多功能表 |  | cPhasePowerFactorPfc | {"en":"C-phase power factor PFc"}
61 | 总功率因数PFs | 16445 | 1 | 0 |  | 690V侧1多功能表 |  | totalPowerFactorPfs | {"en":"Total power factor PFs"}
62 | 频率 | 16446 | 1 | 0 | Hz | 690V侧1多功能表 |  | frequency | {"en":"frequency"}
63 | 总有功电度 | 16447 | 1 | 0 | kWh | 690V侧1多功能表 |  | totalActiveEnergy | {"en":"Total active energy"}
64 | 正向有功电度 | 16448 | 1 | 0 | kWh | 690V侧1多功能表 |  | positiveActiveEnergy | {"en":"Positive active energy"}
65 | 反向有功电度 | 16449 | 1 | 0 | kWh | 690V侧1多功能表 |  | reverseActiveEnergy | {"en":"Reverse active energy"}
66 | 总无功电度 | 16450 | 1 | 0 | kVarh | 690V侧1多功能表 |  | totalReactivePower | {"en":"Total reactive power"}
67 | 正向无功电度 | 16451 | 1 | 0 | kVarh | 690V侧1多功能表 |  | positiveReactivePower | {"en":"Positive reactive power"}
68 | 反向无功电度 | 16452 | 1 | 0 | kVarh | 690V侧1多功能表 |  | reverseReactivePower | {"en":"Reverse reactive power"}
69 | 温度1 | 16453 | 1 | 0 | ℃ | AA2柜温湿度控制器 |  | temperature1 | {"en":"Temperature 1"}
70 | 湿度1 | 16454 | 1 | 0 | %RH | AA2柜温湿度控制器 |  | humidity1 | {"en":"Humidity 1"}
71 | 温度2 | 16455 | 1 | 0 | ℃ | AA2柜温湿度控制器 |  | temperature2 | {"en":"Temperature 2"}
72 | 湿度2 | 16456 | 1 | 0 | %RH | AA2柜温湿度控制器 |  | humidity2 | {"en":"Humidity 2"}
73 | 相电压UA | 16457 | 1 | 0 | V | 690V侧2多功能表 |  | phaseVoltageUa | {"en":"Phase voltage UA"}
74 | 相电压UB | 16458 | 1 | 0 | V | 690V侧2多功能表 |  | phaseVoltageUb | {"en":"Phase voltage UB"}
75 | 相电压UC | 16459 | 1 | 0 | V | 690V侧2多功能表 |  | phaseVoltageUc | {"en":"Phase voltage UC"}
76 | 线电压UAB | 16460 | 1 | 0 | V | 690V侧2多功能表 |  | lineVoltageUab | {"en":"Line voltage UAB"}
77 | 线电压UBC | 16461 | 1 | 0 | V | 690V侧2多功能表 |  | lineVoltageUbc | {"en":"Line voltage UBC"}
78 | 线电压UCA | 16462 | 1 | 0 | V | 690V侧2多功能表 |  | lineVoltageUca | {"en":"Line voltage UCA"}
79 | 相电流IA | 16463 | 1 | 0 | A | 690V侧2多功能表 |  | phaseCurrentIa | {"en":"Phase current IA"}
80 | 相电流IB | 16464 | 1 | 0 | A | 690V侧2多功能表 |  | phaseCurrentIb | {"en":"Phase current IB"}
81 | 相电流IC | 16465 | 1 | 0 | A | 690V侧2多功能表 |  | phaseCurrentIc | {"en":"Phase current IC"}
82 | A相有功功率Pa | 16466 | 1 | 0 | kW | 690V侧2多功能表 |  | aPhaseActivePowerPa | {"en":"A-phase active power Pa"}
83 | B相有功功率Pb | 16467 | 1 | 0 | kW | 690V侧2多功能表 |  | bPhaseActivePowerPb | {"en":"B-phase active power Pb"}
84 | C相有功功率Pc | 16468 | 1 | 0 | kW | 690V侧2多功能表 |  | cPhaseActivePowerPc | {"en":"C-phase active power Pc"}
85 | 总有功功率Ps | 16469 | 1 | 0 | kW | 690V侧2多功能表 |  | totalActivePowerPs | {"en":"Total active power Ps"}
86 | A相无功功率Qa | 16470 | 1 | 0 | kVar | 690V侧2多功能表 |  | aPhaseReactivePowerQa | {"en":"A-phase reactive power Qa"}
87 | B相无功功率Qb | 16471 | 1 | 0 | kVar | 690V侧2多功能表 |  | bPhaseReactivePowerQb | {"en":"B-phase reactive power Qb"}
88 | C相无功功率Qc | 16472 | 1 | 0 | kVar | 690V侧2多功能表 |  | cPhaseReactivePowerQc | {"en":"C-phase reactive power Qc"}
89 | 总无功功率Qs | 16473 | 1 | 0 | kVar | 690V侧2多功能表 |  | totalReactivePowerQs | {"en":"Total reactive power Qs"}
90 | A相视在功率VAa | 16474 | 1 | 0 | kVa | 690V侧2多功能表 |  | aPhaseApparentPowerVaa | {"en":"A-phase apparent power VAa"}
91 | B相视在功率VAb | 16475 | 1 | 0 | kVa | 690V侧2多功能表 |  | bPhaseApparentPowerVab | {"en":"B-phase apparent power VAb"}
92 | C相视在功率VAc | 16476 | 1 | 0 | kVa | 690V侧2多功能表 |  | cPhaseApparentPowerVac | {"en":"C-phase apparent power VAc"}
93 | 总视在功率VAs | 16477 | 1 | 0 | kVa | 690V侧2多功能表 |  | totalApparentPowerVas | {"en":"Total apparent power VAs"}
94 | A相功率因数PFa | 16478 | 1 | 0 |  | 690V侧2多功能表 |  | aPhasePowerFactorPfa | {"en":"A-phase power factor PFa"}
95 | B相功率因数PFb | 16479 | 1 | 0 |  | 690V侧2多功能表 |  | bPhasePowerFactorPfb | {"en":"B-phase power factor PFb"}
96 | C相功率因数PFc | 16480 | 1 | 0 |  | 690V侧2多功能表 |  | cPhasePowerFactorPfc | {"en":"C-phase power factor PFc"}
97 | 总功率因数PFs | 16481 | 1 | 0 |  | 690V侧2多功能表 |  | totalPowerFactorPfs | {"en":"Total power factor PFs"}
98 | 频率 | 16482 | 1 | 0 | Hz | 690V侧2多功能表 |  | frequency | {"en":"frequency"}
99 | 总有功电度 | 16483 | 1 | 0 | kWh | 690V侧2多功能表 |  | totalActiveEnergy | {"en":"Total active energy"}
100 | 正向有功电度 | 16484 | 1 | 0 | kWh | 690V侧2多功能表 |  | positiveActiveEnergy | {"en":"Positive active energy"}
101 | 反向有功电度 | 16485 | 1 | 0 | kWh | 690V侧2多功能表 |  | reverseActiveEnergy | {"en":"Reverse active energy"}
102 | 总无功电度 | 16486 | 1 | 0 | kVarh | 690V侧2多功能表 |  | totalReactivePower | {"en":"Total reactive power"}
103 | 正向无功电度 | 16487 | 1 | 0 | kVarh | 690V侧2多功能表 |  | positiveReactivePower | {"en":"Positive reactive power"}
104 | 反向无功电度 | 16488 | 1 | 0 | kVarh | 690V侧2多功能表 |  | reverseReactivePower | {"en":"Reverse reactive power"}
105 | 温度1 | 16489 | 1 | 0 | ℃ | AA3柜温湿度控制器 |  | temperature1 | {"en":"Temperature 1"}
106 | 湿度1 | 16490 | 1 | 0 | %RH | AA3柜温湿度控制器 |  | humidity1 | {"en":"Humidity 1"}
107 | 温度2 | 16491 | 1 | 0 | ℃ | AA3柜温湿度控制器 |  | temperature2 | {"en":"Temperature 2"}
108 | 湿度2 | 16492 | 1 | 0 | %RH | AA3柜温湿度控制器 |  | humidity2 | {"en":"Humidity 2"}
109 | A相绕组温度 | 16493 | 1 | 0 | ℃ | 主变温控 |  | aPhaseWindingTemperature | {"en":"A-phase winding temperature"}
110 | B相绕组温度 | 16494 | 1 | 0 | ℃ | 主变温控 |  | bPhaseWindingTemperature | {"en":"B-phase winding temperature"}
111 | C相绕组温度 | 16495 | 1 | 0 | ℃ | 主变温控 |  | cPhaseWindingTemperature | {"en":"C-phase winding temperature"}
112 | D相环境温度 | 16496 | 1 | 0 | ℃ | 主变温控 |  | dPhaseAmbientTemperature | {"en":"D-phase ambient temperature"}
113 | E相铁芯温度 | 16497 | 1 | 0 | ℃ | 主变温控 |  | ePhaseIronCoreTemperature | {"en":"E-phase iron core temperature"}

## 遥信
序号 | 名称 | 地址 | 系数 | 偏移 | 单位 | 备注 | 启用 | 键 | 名称翻译
1000 | 400V侧远方位置 | 1 | 1 | 0 |  | 箱变测控 |  | remotePositionOn400vSide | {"en":"Remote position on 400V side"}
1001 | 690V侧1远方位置 | 2 | 1 | 0 |  | 箱变测控 |  | 690vSide1RemotePosition | {"en":"690V side 1 remote position"}
1002 | 690V侧2远方位置 | 3 | 1 | 0 |  | 箱变测控 |  | 690vSide2RemotePosition | {"en":"690V side 2 remote position"}
1003 | 开网门跳闸 | 4 | 1 | 0 |  | 箱变测控 |  | openTheNetworkDoorAndTrip | {"en":"Open the network door and trip"}
1004 | 主变高温告警 | 5 | 1 | 0 |  | 箱变测控 |  | mainTransformerHighTemperatureAlarm | {"en":"Main transformer high temperature alarm"}
1005 | 主变超温跳闸 | 6 | 1 | 0 |  | 箱变测控 |  | mainTransformerOvertemperatureTripping | {"en":"Main transformer overtemperature tripping"}
1006 | 主变温控器故障跳闸 | 7 | 1 | 0 |  | 箱变测控 |  | mainTransformerTemperatureControllerFaultTripped | {"en":"Main transformer temperature controller fault tripped"}
1007 | 主变本体风机故障告警 | 8 | 1 | 0 |  | 箱变测控 |  | mainTransformerBodyFanFaultAlarm | {"en":"Main transformer body fan fault alarm"}
1008 | 主变温控失电跳闸 | 9 | 1 | 0 |  | 箱变测控 |  | mainTransformerTemperatureControlLosesPowerAndTrips | {"en":"Main transformer temperature control loses power and trips"}
1009 | 非电气量保护7 | 10 | 1 | 0 |  | 箱变测控 |  | nonElectricalQuantityProtection7 | {"en":"Non electrical quantity protection 7"}
1010 | 舱体风机热保护告警 | 11 | 1 | 0 |  | 箱变测控 |  | cabinFanThermalProtectionAlarm | {"en":"Cabin fan thermal protection alarm"}
1011 | 非电气量保护9 | 12 | 1 | 0 |  | 箱变测控 |  | nonElectricalQuantityProtection9 | {"en":"Non electrical quantity protection 9"}
1012 | 非电气量保护10 | 13 | 1 | 0 |  | 箱变测控 |  | nonElectricalQuantityProtection10 | {"en":"Non electrical quantity protection 10"}
1013 | 400V侧断路器合闸 | 14 | 1 | 0 |  | 箱变测控 |  | 400vSideCircuitBreakerClosing | {"en":"400V side circuit breaker closing"}
1014 | 400V侧断路器分闸 | 15 | 1 | 0 |  | 箱变测控 |  | 400vSideCircuitBreakerOpens | {"en":"400V side circuit breaker opens"}
1015 | 400V侧断路器合闸准备就绪 | 16 | 1 | 0 |  | 箱变测控 |  | 400vSideCircuitBreakerReadyForClosing | {"en":"400V side circuit breaker ready for closing"}
1016 | 变压器充磁 | 17 | 1 | 0 |  | 箱变测控 |  | transformerMagnetization | {"en":"Transformer magnetization"}
1017 | 400V侧断路器控制电源分位 | 18 | 1 | 0 |  | 箱变测控 |  | 400vSideCircuitBreakerControlPowerSupplyDivision | {"en":"400V side circuit breaker control power supply division"}
1018 | 690V侧1断路器合闸 | 19 | 1 | 0 |  | 箱变测控 |  | 690vSide1CircuitBreakerClosed | {"en":"690V side 1 circuit breaker closed"}
1019 | 690V侧1断路器分闸 | 20 | 1 | 0 |  | 箱变测控 |  | 690vSide1CircuitBreakerOpens | {"en":"690V side 1 circuit breaker opens"}
1020 | 690V侧1断路器合闸准备就绪 | 21 | 1 | 0 |  | 箱变测控 |  | 690vSide1CircuitBreakerIsReadyForClosing | {"en":"690V side 1 circuit breaker is ready for closing"}
1021 | 690V侧1断路器控制电源分位 | 22 | 1 | 0 |  | 箱变测控 |  | 690vSide1CircuitBreakerControlPowerDistribution | {"en":"690V Side 1 Circuit Breaker Control Power Distribution"}
1022 | 自定义开入23 | 23 | 1 | 0 |  | 箱变测控 |  | customInput23 | {"en":"Custom input 23"}
1023 | 690V侧2断路器合闸 | 24 | 1 | 0 |  | 箱变测控 |  | 690vSide2CircuitBreakerClosed | {"en":"690V side 2 circuit breaker closed"}
1024 | 690V侧2断路器分闸 | 25 | 1 | 0 |  | 箱变测控 |  | 690vSide2CircuitBreakerOpens | {"en":"690V side 2 circuit breaker opens"}
1025 | 690V侧2断路器合闸准备就绪 | 26 | 1 | 0 |  | 箱变测控 |  | 690vSide2CircuitBreakerReadyForClosing | {"en":"690V side 2 circuit breaker ready for closing"}
1026 | 690V侧2断路器控制电源分位 | 27 | 1 | 0 |  | 箱变测控 |  | 690vSide2CircuitBreakerControlPowerDistribution | {"en":"690V Side 2 Circuit Breaker Control Power Distribution"}
1027 | 1组散热风机运行 | 28 | 1 | 0 |  | 箱变测控 |  | 1SetOfCoolingFansRunning | {"en":"1 set of cooling fans running"}
1028 | 2组散热风机运行 | 29 | 1 | 0 |  | 箱变测控 |  | twoSetsOfCoolingFansAreRunning | {"en":"Two sets of cooling fans are running"}
1029 | 3组散热风机运行 | 30 | 1 | 0 |  | 箱变测控 |  | threeSetsOfCoolingFansAreRunning | {"en":"Three sets of cooling fans are running"}
1030 | 高压室（400V侧）门开 | 31 | 1 | 0 |  | 箱变测控 |  | highVoltageChamber400vSideDoorOpen | {"en":"High voltage chamber (400V side) door open"}
1031 | 低压室（690V侧）门开 | 32 | 1 | 0 |  | 箱变测控 |  | lowVoltageChamber690vSideDoorOpen | {"en":"Low voltage chamber (690V side) door open"}
1032 | 变压器室门开 | 33 | 1 | 0 |  | 箱变测控 |  | transformerRoomDoorOpen | {"en":"Transformer room door open"}
1033 | 开入34 | 34 | 1 | 0 |  | 箱变测控 |  | entering34 | {"en":"Entering 34"}
1034 | 开入35 | 35 | 1 | 0 |  | 箱变测控 |  | entering35 | {"en":"Entering 35"}
1035 | 开入36 | 36 | 1 | 0 |  | 箱变测控 |  | entering36 | {"en":"Entering 36"}
1036 | 开入37 | 37 | 1 | 0 |  | 箱变测控 |  | entering37 | {"en":"Entering 37"}
1037 | 开入38 | 38 | 1 | 0 |  | 箱变测控 |  | entering38 | {"en":"Entering 38"}
1038 | 开入39 | 39 | 1 | 0 |  | 箱变测控 |  | entering39 | {"en":"Entering 39"}
1039 | 开入40 | 40 | 1 | 0 |  | 箱变测控 |  | enter40 | {"en":"Enter 40"}
1040 | 开入41 | 41 | 1 | 0 |  | 箱变测控 |  | entering41 | {"en":"Entering 41"}
1041 | 异常总信号 | 42 | 1 | 0 |  | 箱变测控 |  | abnormalTotalSignal | {"en":"Abnormal total signal"}
1042 | 跳闸总信号 | 43 | 1 | 0 |  | 箱变测控 |  | totalTrippingSignal | {"en":"Total tripping signal"}
1043 | 告警总信号 | 44 | 1 | 0 |  | 箱变测控 |  | alarmTotalSignal | {"en":"Alarm total signal"}

## 遥控
序号 | 名称 | 地址 | 系数 | 偏移 | 单位 | 备注 | 启用 | 键 | 名称翻译
3000 | 400V侧遥控开关 | 24577 | 1 | 0 |  | 箱变测控 |  | 400vSideRemoteControlSwitch | {"en":"400V side remote control switch"}
3001 | 690V侧1遥控开关 | 24578 | 1 | 0 |  | 箱变测控 |  | 690vSide1RemoteControlSwitch | {"en":"690V side 1 remote control switch"}
3002 | 复归 | 24579 | 1 | 0 |  | 箱变测控 |  | return | {"en":"return"}
3003 | 690V侧2遥控开关 | 24580 | 1 | 0 |  | 箱变测控 |  | 690vSide2RemoteControlSwitch | {"en":"690V side 2 remote control switch"}