## 遥测
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位
1 | 电池簇总数量 | U16 |  |  | 7001 | InputRegisters | 2 | ABCD | 1 | 0 |  | totalNumberOfBatteryClusters | {"en":"Total number of battery clusters"}
2 | 启用电池簇数量 | U16 |  |  | 7002 | InputRegisters | 2 | ABCD | 1 | 0 |  | enableTheNumberOfBatteryClusters | {"en":"Enable the number of battery clusters"}
3 | 电池堆SOC | U16 | % |  | 7003 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | batteryStackSoc | {"en":"Battery stack SOC"}
4 | 电池堆总电压 | U16 | V |  | 7004 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | totalVoltageOfBatteryStack | {"en":"Total voltage of battery stack"}
5 | 电池堆总电流 | I16 | A |  | 7005 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | totalCurrentOfBatteryStack | {"en":"Total current of battery stack"}
6 | 电池堆SOH | U16 | % |  | 7006 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | batteryStackSoh | {"en":"Battery stack SOH"}
7 | 堆单体平均电压 | U16 | mV |  | 7007 | InputRegisters | 2 | ABCD | 1 | 0 |  | averageVoltageOfStackCells | {"en":"Average voltage of stack cells"}
8 | 堆单体平均温度 | U16 | ℃ |  | 7008 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | averageTemperatureOfIndividualReactorCells | {"en":"Average temperature of individual reactor cells"}
9 | 堆最高单体电压 | U16 | mV |  | 7009 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumIndividualVoltageOfTheStack | {"en":"Maximum individual voltage of the stack"}
10 | 堆最高单体电压编号 | U16 |  |  | 7010 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumIndividualVoltageCodeOfTheStack | {"en":"Maximum individual voltage code of the stack"}
11 | 堆最低单体电压 | U16 | mV |  | 7011 | InputRegisters | 2 | ABCD | 1 | 0 |  | minimumCellVoltageOfTheStack | {"en":"Minimum cell voltage of the stack"}
12 | 堆最低单体电压编号 | U16 |  |  | 7012 | InputRegisters | 2 | ABCD | 1 | 0 |  | minimumIndividualVoltageCodeOfTheStack | {"en":"Minimum individual voltage code of the stack"}
13 | 堆次高单体电压 | U16 | mV |  | 7013 | InputRegisters | 2 | ABCD | 1 | 0 |  | stackedHighCellVoltage | {"en":"Stacked high cell voltage"}
14 | 堆次高单体电压编号 | U16 |  |  | 7014 | InputRegisters | 2 | ABCD | 1 | 0 |  | stackedHighCellVoltageNumber | {"en":"Stacked high cell voltage number"}
15 | 堆次低单体电压 | U16 | mV |  | 7015 | InputRegisters | 2 | ABCD | 1 | 0 |  | lowCellVoltageInTheStack | {"en":"Low cell voltage in the stack"}
16 | 堆次低单体电压编号 | U16 |  |  | 7016 | InputRegisters | 2 | ABCD | 1 | 0 |  | lowCellVoltageNumberOfStack | {"en":"Low cell voltage number of stack"}
17 | 堆最高单体温度 | U16 | ℃ |  | 7017 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | maximumIndividualTemperatureOfTheStack | {"en":"Maximum individual temperature of the stack"}
18 | 堆最高单体温度编号 | U16 |  |  | 7018 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumIndividualTemperatureCodeOfTheStack | {"en":"Maximum individual temperature code of the stack"}
19 | 堆最低单体温度 | U16 | ℃ |  | 7019 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | minimumIndividualTemperatureOfTheStack | {"en":"Minimum individual temperature of the stack"}
20 | 堆最低单体温度编号 | U16 |  |  | 7020 | InputRegisters | 2 | ABCD | 1 | 0 |  | minimumIndividualTemperatureCodeOfTheStack | {"en":"Minimum individual temperature code of the stack"}
21 | 堆次高单体温度 | U16 | ℃ |  | 7021 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | highTemperatureOfIndividualCellsInTheStack | {"en":"High temperature of individual cells in the stack"}
22 | 堆次高单体温度编号 | U16 |  |  | 7022 | InputRegisters | 2 | ABCD | 1 | 0 |  | unitTemperatureNumberForHighStackLevel | {"en":"Unit temperature number for high stack level"}
23 | 堆次低单体温度 | U16 | ℃ |  | 7023 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | lowIndividualTemperatureInTheStack | {"en":"Low individual temperature in the stack"}
24 | 堆次低单体温度编号 | U16 |  |  | 7024 | InputRegisters | 2 | ABCD | 1 | 0 |  | lowIndividualTemperatureCodeForStackLevel | {"en":"Low individual temperature code for stack level"}
25 | 堆内单体电压极差 | U16 | mV |  | 7025 | InputRegisters | 2 | ABCD | 1 | 0 |  | voltageRangeOfIndividualCellsInsideTheReactor | {"en":"Voltage range of individual cells inside the reactor"}
26 | 电池堆系统温差 | U16 | ℃ |  | 7026 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | temperatureDifferenceOfBatteryStackSystem | {"en":"Temperature difference of battery stack system"}
27 | 电池堆绝缘阻值 | U16 | kΩ |  | 7027 | InputRegisters | 2 | ABCD | 1 | 0 |  | insulationResistanceOfBatteryStack | {"en":"Insulation resistance of battery stack"}
28 | 堆最大允许放电功率 | U16 | kW |  | 7028 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumAllowableDischargePowerOfTheStack | {"en":"Maximum allowable discharge power of the stack"}
29 | 堆最大允许充电功率 | U16 | kW |  | 7029 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumAllowableChargingPowerOfThePile | {"en":"Maximum allowable charging power of the pile"}
30 | 堆最大允许充电电流 | U16 | A |  | 7030 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | maximumAllowableChargingCurrentForThePile | {"en":"Maximum allowable charging current for the pile"}
31 | 堆最大允许放电电流 | U16 | A |  | 7031 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | maximumAllowableDischargeCurrentOfTheStack | {"en":"Maximum allowable discharge current of the stack"}
32 | 堆最大允许充电电压 | U16 | V |  | 7032 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | maximumAllowableChargingVoltageForTheStack | {"en":"Maximum allowable charging voltage for the stack"}
33 | 堆最大允许放电电压 | U16 | V |  | 7033 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | maximumAllowableDischargeVoltageOfTheStack | {"en":"Maximum allowable discharge voltage of the stack"}
34 | 堆可放电量 | U32 | kWh |  | 7034 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | stackableDischargeCapacity | {"en":"Stackable discharge capacity"}
35 | 堆可充电量 | U32 | kWh |  | 7036 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | stackableChargingCapacity | {"en":"Stackable charging capacity"}
36 | 堆日放电电量 | U32 | kWh |  | 7038 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | dailyDischargeCapacityOfThePile | {"en":"Daily discharge capacity of the pile"}
37 | 堆日充电电量 | U32 | kWh |  | 7040 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | dailyChargingCapacity | {"en":"Daily charging capacity"}
38 | 堆累计放电电量 | U32 | kWh |  | 7042 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | accumulatedDischargePowerOfThePile | {"en":"Accumulated discharge power of the pile"}
39 | 堆累计充电电量 | U32 | kWh |  | 7044 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | accumulatedChargingCapacityOfThePile | {"en":"Accumulated charging capacity of the pile"}
40 | 堆标称电量 | U32 | kWh |  | 7046 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | nominalPowerConsumptionOfThePile | {"en":"Nominal power consumption of the pile"}
41 | 堆充放电标定/复位状态 （功能预留） | U16 |  |  | 7048 | InputRegisters | 2 | ABCD | 1 | 0 |  | calibrationResetStatusOfStackChargingAndDischarging | {"en":"Calibration/reset status of stack charging and discharging"}
42 | EMU/BAMU时间（年） | U16 |  |  | 7049 | InputRegisters | 2 | ABCD | 1 | 0 |  | emuBauTimeYear | {"en":"EMU/BAU time (year)"}
43 | EMU/BAMU时间（月） | U16 |  |  | 7050 | InputRegisters | 2 | ABCD | 1 | 0 |  | emuBauTimeMonth | {"en":"EMU/BAU time (month)"}
44 | EMU/BAMU时间（日） | U16 |  |  | 7051 | InputRegisters | 2 | ABCD | 1 | 0 |  | emuBauTimeDay | {"en":"EMU/BAU time (day)"}
45 | EMU/BAMU时间（时） | U16 |  |  | 7052 | InputRegisters | 2 | ABCD | 1 | 0 |  | emuBamuTimeHours | {"en":"EMU/BAMU time (hours)"}
46 | EMU/BAMU时间（分） | U16 |  |  | 7053 | InputRegisters | 2 | ABCD | 1 | 0 |  | emuBauTimeMinutes | {"en":"EMU/BAU time (minutes)"}
47 | EMU/BAMU时间（秒） | U16 |  |  | 7054 | InputRegisters | 2 | ABCD | 1 | 0 |  | emuBauTimeSeconds | {"en":"EMU/BAU time (seconds)"}
48 | BMS看门狗 | U16 |  |  | 7055 | InputRegisters | 2 | ABCD | 1 | 0 |  | bmsWatchdog | {"en":"BMS watchdog"}
49 | BAMU 软件版本号1 | U16 |  |  | 7056 | InputRegisters | 2 | ABCD | 1 | 0 |  | bamuSoftwareVersion1 | {"en":"BAMU software version 1"}
50 | BAMU 软件版本号2 | U16 |  |  | 7057 | InputRegisters | 2 | ABCD | 1 | 0 |  | bamuSoftwareVersion2 | {"en":"BAMU software version 2"}
51 | BAMU 软件版本号3 | U16 |  |  | 7058 | InputRegisters | 2 | ABCD | 1 | 0 |  | bamuSoftwareVersionNumber3 | {"en":"BAMU software version number 3"}
52 | BAMU 软件版本号4 | U16 |  |  | 7059 | InputRegisters | 2 | ABCD | 1 | 0 |  | bamuSoftwareVersionNumber4 | {"en":"BAMU software version number 4"}
100 | 簇 1 电池簇SOC | U16 | % |  | 9001 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster1BatteryClusterSoc | {"en":"Cluster 1 battery cluster SOC"}
101 | 簇 1 电池簇电压 | U16 | V |  | 9002 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster1BatteryClusterVoltage | {"en":"Cluster 1 battery cluster voltage"}
102 | 簇 1 电池簇电流 | I16 | A |  | 9003 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster1BatteryClusterCurrent | {"en":"Cluster 1 battery cluster current"}
103 | 簇 1 电池簇SOH | U16 | % |  | 9004 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster1BatteryClusterSoh | {"en":"Cluster 1 battery cluster SOH"}
104 | 簇 1 簇单体平均电压 | U16 | mV |  | 9005 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1AverageVoltageOfIndividualCells | {"en":"Cluster 1 average voltage of individual cells"}
105 | 簇 1 簇单体平均温度 | U16 | ℃ |  | 9006 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | averageTemperatureOfCluster1Monomer | {"en":"Average temperature of cluster 1 monomer"}
106 | 簇 1 簇最高单体电压 | U16 | mV |  | 9007 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1HighestSingleCellVoltage | {"en":"Cluster 1, highest single cell voltage"}
107 | 簇 1 簇最高单体电压编号 | U16 |  |  | 9008 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1HighestSingleCellVoltageNumber | {"en":"Cluster 1 highest single cell voltage number"}
108 | 簇 1 簇最低单体电压值 | U16 | mV |  | 9009 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1HasTheLowestSingleCellVoltageValue | {"en":"Cluster 1 has the lowest single cell voltage value"}
109 | 簇 1 簇最低单体电压编号 | U16 |  |  | 9010 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1LowestSingleCellVoltageNumber | {"en":"Cluster 1, lowest single cell voltage number"}
110 | 簇 1 簇次高单体电压 | U16 | mV |  | 9011 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1Cluster2HighSingleCellVoltage | {"en":"Cluster 1, Cluster 2, High Single Cell Voltage"}
111 | 簇 1 簇次高单体电压编号 | U16 |  |  | 9012 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1ClusterSecondaryHighCellVoltageNumber | {"en":"Cluster 1 cluster secondary high cell voltage number"}
112 | 簇 1 簇次低单体电压 | U16 | mV |  | 9013 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1ClusterSecondaryLowCellVoltage | {"en":"Cluster 1, cluster secondary, low cell voltage"}
113 | 簇 1 簇次低单体电压编号 | U16 |  |  | 9014 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1Cluster2LowCellVoltageNumber | {"en":"Cluster 1, Cluster 2, Low Cell Voltage Number"}
114 | 簇 1 簇最高单体温度 | U16 | ℃ |  | 9015 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster1HighestMonomerTemperature | {"en":"Cluster 1 highest monomer temperature"}
115 | 簇 1 簇最高单体温度编号 | U16 |  |  | 9016 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1HighestMonomerTemperatureNumber | {"en":"Cluster 1 highest monomer temperature number"}
116 | 簇 1 簇最低单体温度 | U16 | ℃ |  | 9017 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster1LowestMonomerTemperature | {"en":"Cluster 1 lowest monomer temperature"}
117 | 簇 1 簇最低单体温度编号 | U16 |  |  | 9018 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1LowestMonomerTemperatureNumber | {"en":"Cluster 1 lowest monomer temperature number"}
118 | 簇 1 簇次高单体温度 | U16 | ℃ |  | 9019 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster1Cluster2HighMonomerTemperature | {"en":"Cluster 1, cluster 2, high monomer temperature"}
119 | 簇 1 簇次高单体温度编号 | U16 |  |  | 9020 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1Cluster2HighMonomerTemperatureNumber | {"en":"Cluster 1, cluster 2, high monomer temperature number"}
120 | 簇 1 簇次低单体温度 | U16 | ℃ |  | 9021 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster1Cluster2LowMonomerTemperature | {"en":"Cluster 1, cluster 2, low monomer temperature"}
121 | 簇 1 簇次低单体温度编号 | U16 |  |  | 9022 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1ClusterNumberLowMonomerTemperature | {"en":"Cluster 1, cluster number, low monomer temperature"}
122 | 簇 1 簇内单体电压极差 | U16 | mV |  | 9023 | InputRegisters | 2 | ABCD | 1 | 0 |  | voltageRangeOfIndividualCellsWithinCluster1 | {"en":"Voltage range of individual cells within cluster 1"}
123 | 簇 1 簇内单体温度极差 | U16 | ℃ |  | 9024 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | temperatureRangeOfMonomersWithinCluster1 | {"en":"Temperature range of monomers within cluster 1"}
124 | 簇 1 簇正母线对地绝缘阻值 | U16 | kΩ |  | 9025 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1PositiveBusbarInsulationResistanceToGround | {"en":"Cluster 1 positive busbar insulation resistance to ground"}
125 | 簇 1 簇负母线对地绝缘阻值 | U16 | kΩ |  | 9026 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1NegativeBusbarInsulationResistanceToGround | {"en":"Cluster 1 negative busbar insulation resistance to ground"}
126 | 簇 1 簇最大允许放电功率 | U16 | kW |  | 9027 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1MaximumAllowableDischargePower | {"en":"Cluster 1 Maximum allowable discharge power"}
127 | 簇 1 簇最大允许充电功率 | U16 | kW |  | 9028 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1MaximumAllowableChargingPower | {"en":"Cluster 1 Maximum allowable charging power"}
128 | 簇 1 BCMU 软件版本号1 | U16 |  |  | 9029 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1BcmuSoftwareVersionNumber1 | {"en":"Cluster 1 BCMU software version number 1"}
129 | 簇 1 BCMU 软件版本号2 | U16 |  |  | 9030 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1BcmuSoftwareVersion2 | {"en":"Cluster 1 BCMU software version 2"}
130 | 簇 1 BCMU 软件版本号3 | U16 |  |  | 9031 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1BcmuSoftwareVersionNumber3 | {"en":"Cluster 1 BCMU software version number 3"}
131 | 簇 1 BCMU 软件版本号4 | U16 |  |  | 9032 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster1BcmuSoftwareVersionNumber4 | {"en":"Cluster 1 BCMU software version number 4"}
132 | 簇 1 包总压压差 | U16 | V |  | 9035 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster1PackageTotalPressureDifference | {"en":"Cluster 1 package total pressure difference"}
133 | 簇 1 簇日放电电量 | U32 | kWh |  | 9037 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster1DailyDischargeElectricity | {"en":"Cluster 1 daily discharge electricity"}
134 | 簇 1 簇日充电电量 | U32 | kWh |  | 9039 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster1DailyChargingCapacity | {"en":"Cluster 1 daily charging capacity"}
135 | 簇 1 簇累计放电电量 | U32 | kWh |  | 9041 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster1CumulativeDischargePower | {"en":"Cluster 1 cumulative discharge power"}
136 | 簇 1 簇累计充电电量 | U32 | kWh |  | 9043 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster1AccumulatedChargingCapacity | {"en":"Cluster 1 Accumulated Charging Capacity"}
137 | 簇 1 簇可放电量 | U32 | kWh |  | 9045 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster1CanDischargeElectricity | {"en":"Cluster 1 can discharge electricity"}
138 | 簇 1 簇可充电量 | U32 | kWh |  | 9047 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster1RechargeableCapacity | {"en":"Cluster 1 rechargeable capacity"}
139 | 簇 2 电池簇SOC | U16 | % |  | 9049 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster2BatteryClusterSoc | {"en":"Cluster 2 battery cluster SOC"}
140 | 簇 2 电池簇电压 | U16 | V |  | 9050 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster2BatteryClusterVoltage | {"en":"Cluster 2 battery cluster voltage"}
141 | 簇 2 电池簇电流 | I16 | A |  | 9051 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster2BatteryClusterCurrent | {"en":"Cluster 2 battery cluster current"}
142 | 簇 2 电池簇SOH | U16 | % |  | 9052 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster2BatteryClusterSoh | {"en":"Cluster 2 battery cluster SOH"}
143 | 簇 2 簇单体平均电压 | U16 | mV |  | 9053 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2AverageVoltageOfIndividualCells | {"en":"Cluster 2 average voltage of individual cells"}
144 | 簇 2 簇单体平均温度 | U16 | ℃ |  | 9054 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | averageTemperatureOfCluster2Monomers | {"en":"Average temperature of cluster 2 monomers"}
145 | 簇 2 簇最高单体电压 | U16 | mV |  | 9055 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2HighestSingleCellVoltage | {"en":"Cluster 2, highest single cell voltage"}
146 | 簇 2 簇最高单体电压编号 | U16 |  |  | 9056 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2HighestSingleCellVoltageNumber | {"en":"Cluster 2 highest single cell voltage number"}
147 | 簇 2 簇最低单体电压值 | U16 | mV |  | 9057 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2LowestSingleCellVoltageValue | {"en":"Cluster 2, lowest single cell voltage value"}
148 | 簇 2 簇最低单体电压编号 | U16 |  |  | 9058 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2LowestSingleCellVoltageNumber | {"en":"Cluster 2, lowest single cell voltage number"}
149 | 簇 2 簇次高单体电压 | U16 | mV |  | 9059 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2SecondaryHighCellVoltage | {"en":"Cluster 2, secondary high cell voltage"}
150 | 簇 2 簇次高单体电压编号 | U16 |  |  | 9060 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2Cluster2SecondaryHighCellVoltageNumber | {"en":"Cluster 2, Cluster 2, Secondary High Cell Voltage Number"}
151 | 簇 2 簇次低单体电压 | U16 | mV |  | 9061 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2Cluster2LowCellVoltage | {"en":"Cluster 2, cluster 2, low cell voltage"}
152 | 簇 2 簇次低单体电压编号 | U16 |  |  | 9062 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2Cluster2LowCellVoltageNumber | {"en":"Cluster 2, Cluster 2, Low Cell Voltage Number"}
153 | 簇 2 簇最高单体温度 | U16 | ℃ |  | 9063 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster2HighestMonomerTemperature | {"en":"Cluster 2 highest monomer temperature"}
154 | 簇 2 簇最高单体温度编号 | U16 |  |  | 9064 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2HighestMonomerTemperatureNumber | {"en":"Cluster 2 highest monomer temperature number"}
155 | 簇 2 簇最低单体温度 | U16 | ℃ |  | 9065 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster2LowestMonomerTemperature | {"en":"Cluster 2 lowest monomer temperature"}
156 | 簇 2 簇最低单体温度编号 | U16 |  |  | 9066 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2LowestMonomerTemperatureNumber | {"en":"Cluster 2 lowest monomer temperature number"}
157 | 簇 2 簇次高单体温度 | U16 | ℃ |  | 9067 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster2SecondaryHighMonomerTemperature | {"en":"Cluster 2, secondary high monomer temperature"}
158 | 簇 2 簇次高单体温度编号 | U16 |  |  | 9068 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2SecondaryHighMonomerTemperatureNumber | {"en":"Cluster 2, secondary high monomer temperature number"}
159 | 簇 2 簇次低单体温度 | U16 | ℃ |  | 9069 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster2Cluster2LowMonomerTemperature | {"en":"Cluster 2, cluster 2, low monomer temperature"}
160 | 簇 2 簇次低单体温度编号 | U16 |  |  | 9070 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2Cluster2LowSingleUnitTemperatureNumber | {"en":"Cluster 2, Cluster 2, Low Single Unit Temperature Number"}
161 | 簇 2 簇内单体电压极差 | U16 | mV |  | 9071 | InputRegisters | 2 | ABCD | 1 | 0 |  | voltageRangeOfIndividualCellsWithinCluster2 | {"en":"Voltage range of individual cells within cluster 2"}
162 | 簇 2 簇内单体温度极差 | U16 | ℃ |  | 9072 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | temperatureRangeOfMonomersWithinCluster2 | {"en":"Temperature range of monomers within cluster 2"}
163 | 簇 2 簇正母线对地绝缘阻值 | U16 | kΩ |  | 9073 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2PositiveBusbarInsulationResistanceToGround | {"en":"Cluster 2 positive busbar insulation resistance to ground"}
164 | 簇 2 簇负母线对地绝缘阻值 | U16 | kΩ |  | 9074 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2NegativeBusInsulationResistanceToGround | {"en":"Cluster 2 negative bus insulation resistance to ground"}
165 | 簇 2 簇最大允许放电功率 | U16 | kW |  | 9075 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumAllowableDischargePowerForCluster2 | {"en":"Maximum allowable discharge power for cluster 2"}
166 | 簇 2 簇最大允许充电功率 | U16 | kW |  | 9076 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumAllowableChargingPowerForCluster2 | {"en":"Maximum allowable charging power for cluster 2"}
167 | 簇 2 BCMU 软件版本号1 | U16 |  |  | 9077 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2BcmuSoftwareVersionNumber1 | {"en":"Cluster 2 BCMU software version number 1"}
168 | 簇 2 BCMU 软件版本号2 | U16 |  |  | 9078 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2BcmuSoftwareVersionNumber2 | {"en":"Cluster 2 BCMU software version number 2"}
169 | 簇 2 BCMU 软件版本号3 | U16 |  |  | 9079 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2BcmuSoftwareVersionNumber3 | {"en":"Cluster 2 BCMU software version number 3"}
170 | 簇 2 BCMU 软件版本号4 | U16 |  |  | 9080 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster2BcmuSoftwareVersionNumber4 | {"en":"Cluster 2 BCMU software version number 4"}
171 | 簇 2 包总压压差 | U16 | V |  | 9083 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster2PackageTotalPressureDifference | {"en":"Cluster 2 package total pressure difference"}
172 | 簇 2 簇日放电电量 | U32 | kWh |  | 9085 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster2DailyDischargeElectricity | {"en":"Cluster 2 daily discharge electricity"}
173 | 簇 2 簇日充电电量 | U32 | kWh |  | 9087 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster2DailyChargingCapacity | {"en":"Cluster 2 daily charging capacity"}
174 | 簇 2 簇累计放电电量 | U32 | kWh |  | 9089 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | accumulatedDischargePowerOfCluster2 | {"en":"Accumulated discharge power of cluster 2"}
175 | 簇 2 簇累计充电电量 | U32 | kWh |  | 9091 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster2AccumulatedChargingCapacity | {"en":"Cluster 2 Accumulated Charging Capacity"}
176 | 簇 2 簇可放电量 | U32 | kWh |  | 9093 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster2CanDischargeElectricity | {"en":"Cluster 2 can discharge electricity"}
177 | 簇 2 簇可充电量 | U32 | kWh |  | 9095 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster2RechargeableCapacity | {"en":"Cluster 2 rechargeable capacity"}
178 | 簇 3 电池簇SOC | U16 | % |  | 9097 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster3BatteryClusterSoc | {"en":"Cluster 3 battery cluster SOC"}
179 | 簇 3 电池簇电压 | U16 | V |  | 9098 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster3BatteryClusterVoltage | {"en":"Cluster 3 battery cluster voltage"}
180 | 簇 3 电池簇电流 | I16 | A |  | 9099 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster3BatteryClusterCurrent | {"en":"Cluster 3 battery cluster current"}
181 | 簇 3 电池簇SOH | U16 | % |  | 9100 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster3BatteryClusterSoh | {"en":"Cluster 3 battery cluster SOH"}
182 | 簇 3 簇单体平均电压 | U16 | mV |  | 9101 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3AverageVoltageOfIndividualCells | {"en":"Cluster 3 average voltage of individual cells"}
183 | 簇 3 簇单体平均温度 | U16 | ℃ |  | 9102 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | averageTemperatureOfCluster3Monomers | {"en":"Average temperature of cluster 3 monomers"}
184 | 簇 3 簇最高单体电压 | U16 | mV |  | 9103 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3HighestSingleCellVoltage | {"en":"Cluster 3, highest single cell voltage"}
185 | 簇 3 簇最高单体电压编号 | U16 |  |  | 9104 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3HighestSingleCellVoltageNumber | {"en":"Cluster 3, highest single cell voltage number"}
186 | 簇 3 簇最低单体电压值 | U16 | mV |  | 9105 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3LowestSingleCellVoltageValue | {"en":"Cluster 3, lowest single cell voltage value"}
187 | 簇 3 簇最低单体电压编号 | U16 |  |  | 9106 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3LowestSingleCellVoltageNumber | {"en":"Cluster 3, lowest single cell voltage number"}
188 | 簇 3 簇次高单体电压 | U16 | mV |  | 9107 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3SecondaryHighCellVoltage | {"en":"Cluster 3, secondary high cell voltage"}
189 | 簇 3 簇次高单体电压编号 | U16 |  |  | 9108 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3SecondaryHighCellVoltageNumber | {"en":"Cluster 3, secondary high cell voltage number"}
190 | 簇 3 簇次低单体电压 | U16 | mV |  | 9109 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3ClusterSubLowCellVoltage | {"en":"Cluster 3, cluster sub low cell voltage"}
191 | 簇 3 簇次低单体电压编号 | U16 |  |  | 9110 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3Cluster2LowCellVoltageNumber | {"en":"Cluster 3, Cluster 2, Low Cell Voltage Number"}
192 | 簇 3 簇最高单体温度 | U16 | ℃ |  | 9111 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster3HighestMonomerTemperature | {"en":"Cluster 3 highest monomer temperature"}
193 | 簇 3 簇最高单体温度编号 | U16 |  |  | 9112 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3HighestMonomerTemperatureNumber | {"en":"Cluster 3 highest monomer temperature number"}
194 | 簇 3 簇最低单体温度 | U16 | ℃ |  | 9113 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster3LowestMonomerTemperature | {"en":"Cluster 3 lowest monomer temperature"}
195 | 簇 3 簇最低单体温度编号 | U16 |  |  | 9114 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3LowestMonomerTemperatureNumber | {"en":"Cluster 3 lowest monomer temperature number"}
196 | 簇 3 簇次高单体温度 | U16 | ℃ |  | 9115 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster3SubHighMonomerTemperature | {"en":"Cluster 3, sub high monomer temperature"}
197 | 簇 3 簇次高单体温度编号 | U16 |  |  | 9116 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3SubHighMonomerTemperatureNumber | {"en":"Cluster 3, sub high monomer temperature number"}
198 | 簇 3 簇次低单体温度 | U16 | ℃ |  | 9117 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster3ClustersWithLowMonomerTemperature | {"en":"Cluster 3 clusters with low monomer temperature"}
199 | 簇 3 簇次低单体温度编号 | U16 |  |  | 9118 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3ClusterNumberLowMonomerTemperature | {"en":"Cluster 3, cluster number, low monomer temperature"}
200 | 簇 3 簇内单体电压极差 | U16 | mV |  | 9119 | InputRegisters | 2 | ABCD | 1 | 0 |  | voltageRangeOfIndividualCellsWithinCluster3 | {"en":"Voltage range of individual cells within cluster 3"}
201 | 簇 3 簇内单体温度极差 | U16 | ℃ |  | 9120 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | temperatureRangeOfMonomersWithinCluster3 | {"en":"Temperature range of monomers within cluster 3"}
202 | 簇 3 簇正母线对地绝缘阻值 | U16 | kΩ |  | 9121 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3PositiveBusbarInsulationResistanceToGround | {"en":"Cluster 3 positive busbar insulation resistance to ground"}
203 | 簇 3 簇负母线对地绝缘阻值 | U16 | kΩ |  | 9122 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3NegativeBusInsulationResistanceToGround | {"en":"Cluster 3 negative bus insulation resistance to ground"}
204 | 簇 3 簇最大允许放电功率 | U16 | kW |  | 9123 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumAllowableDischargePowerForCluster3 | {"en":"Maximum allowable discharge power for cluster 3"}
205 | 簇 3 簇最大允许充电功率 | U16 | kW |  | 9124 | InputRegisters | 2 | ABCD | 1 | 0 |  | maximumAllowableChargingPowerForCluster3 | {"en":"Maximum allowable charging power for cluster 3"}
206 | 簇 3 BCMU 软件版本号1 | U16 |  |  | 9125 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3BcmuSoftwareVersion1 | {"en":"Cluster 3 BCMU software version 1"}
207 | 簇 3 BCMU 软件版本号2 | U16 |  |  | 9126 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3BcmuSoftwareVersion2 | {"en":"Cluster 3 BCMU software version 2"}
208 | 簇 3 BCMU 软件版本号3 | U16 |  |  | 9127 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3BcmuSoftwareVersionNumber3 | {"en":"Cluster 3 BCMU software version number 3"}
209 | 簇 3 BCMU 软件版本号4 | U16 |  |  | 9128 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster3BcmuSoftwareVersionNumber4 | {"en":"Cluster 3 BCMU software version number 4"}
210 | 簇 3 包总压压差 | U16 | V |  | 9131 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster3PackageTotalPressureDifference | {"en":"Cluster 3 package total pressure difference"}
211 | 簇 3 簇日放电电量 | U32 | kWh |  | 9133 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster3DailyDischargeElectricity | {"en":"Cluster 3 daily discharge electricity"}
212 | 簇 3 簇日充电电量 | U32 | kWh |  | 9135 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster3DailyChargingCapacity | {"en":"Cluster 3 daily charging capacity"}
213 | 簇 3 簇累计放电电量 | U32 | kWh |  | 9137 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | accumulatedDischargePowerOfCluster3 | {"en":"Accumulated discharge power of cluster 3"}
214 | 簇 3 簇累计充电电量 | U32 | kWh |  | 9139 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster3AccumulatedChargingCapacity | {"en":"Cluster 3 Accumulated Charging Capacity"}
215 | 簇 3 簇可放电量 | U32 | kWh |  | 9141 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster3CanDischargeElectricity | {"en":"Cluster 3 can discharge electricity"}
216 | 簇 3 簇可充电量 | U32 | kWh |  | 9143 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster3RechargeableCapacity | {"en":"Cluster 3 rechargeable capacity"}
217 | 簇 4 电池簇SOC | U16 | % |  | 9145 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster4BatteryClusterSoc | {"en":"Cluster 4 battery cluster SOC"}
218 | 簇 4 电池簇电压 | U16 | V |  | 9146 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster4BatteryClusterVoltage | {"en":"Cluster 4 battery cluster voltage"}
219 | 簇 4 电池簇电流 | I16 | A |  | 9147 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster4BatteryClusterCurrent | {"en":"Cluster 4 battery cluster current"}
220 | 簇 4 电池簇SOH | U16 | % |  | 9148 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster4BatteryClusterSoh | {"en":"Cluster 4 battery cluster SOH"}
221 | 簇 4 簇单体平均电压 | U16 | mV |  | 9149 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4AverageVoltageOfIndividualCells | {"en":"Cluster 4 average voltage of individual cells"}
222 | 簇 4 簇单体平均温度 | U16 | ℃ |  | 9150 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | averageTemperatureOfCluster4Monomers | {"en":"Average temperature of cluster 4 monomers"}
223 | 簇 4 簇最高单体电压 | U16 | mV |  | 9151 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4HighestSingleCellVoltage | {"en":"Cluster 4, highest single cell voltage"}
224 | 簇 4 簇最高单体电压编号 | U16 |  |  | 9152 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4HighestSingleCellVoltageNumber | {"en":"Cluster 4, highest single cell voltage number"}
225 | 簇 4 簇最低单体电压值 | U16 | mV |  | 9153 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4LowestSingleCellVoltageValue | {"en":"Cluster 4, lowest single cell voltage value"}
226 | 簇 4 簇最低单体电压编号 | U16 |  |  | 9154 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4LowestSingleCellVoltageNumber | {"en":"Cluster 4, lowest single cell voltage number"}
227 | 簇 4 簇次高单体电压 | U16 | mV |  | 9155 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4SubHighSingleCellVoltage | {"en":"Cluster 4, sub high single cell voltage"}
228 | 簇 4 簇次高单体电压编号 | U16 |  |  | 9156 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4SecondaryHighCellVoltageNumber | {"en":"Cluster 4, secondary high cell voltage number"}
229 | 簇 4 簇次低单体电压 | U16 | mV |  | 9157 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4ClustersWithLowCellVoltage | {"en":"Cluster 4 clusters with low cell voltage"}
230 | 簇 4 簇次低单体电压编号 | U16 |  |  | 9158 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4Cluster2LowCellVoltageNumber | {"en":"Cluster 4, Cluster 2, Low Cell Voltage Number"}
231 | 簇 4 簇最高单体温度 | U16 | ℃ |  | 9159 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster4HighestMonomerTemperature | {"en":"Cluster 4 highest monomer temperature"}
232 | 簇 4 簇最高单体温度编号 | U16 |  |  | 9160 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4HighestMonomerTemperatureNumber | {"en":"Cluster 4, highest monomer temperature number"}
233 | 簇 4 簇最低单体温度 | U16 | ℃ |  | 9161 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster4LowestMonomerTemperature | {"en":"Cluster 4 lowest monomer temperature"}
234 | 簇 4 簇最低单体温度编号 | U16 |  |  | 9162 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4LowestMonomerTemperatureNumber | {"en":"Cluster 4 lowest monomer temperature number"}
235 | 簇 4 簇次高单体温度 | U16 | ℃ |  | 9163 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster4SubHighMonomerTemperature | {"en":"Cluster 4, sub high monomer temperature"}
236 | 簇 4 簇次高单体温度编号 | U16 |  |  | 9164 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4SubHighMonomerTemperatureNumber | {"en":"Cluster 4, sub high monomer temperature number"}
237 | 簇 4 簇次低单体温度 | U16 | ℃ |  | 9165 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster4ClustersWithLowMonomerTemperature | {"en":"Cluster 4 clusters with low monomer temperature"}
238 | 簇 4 簇次低单体温度编号 | U16 |  |  | 9166 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4ClusterNumberLowMonomerTemperature | {"en":"Cluster 4, cluster number, low monomer temperature"}
239 | 簇 4 簇内单体电压极差 | U16 | mV |  | 9167 | InputRegisters | 2 | ABCD | 1 | 0 |  | voltageRangeOfIndividualCellsWithinCluster4 | {"en":"Voltage range of individual cells within cluster 4"}
240 | 簇 4 簇内单体温度极差 | U16 | ℃ |  | 9168 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | temperatureRangeOfMonomersWithinCluster4 | {"en":"Temperature range of monomers within cluster 4"}
241 | 簇 4 簇正母线对地绝缘阻值 | U16 | kΩ |  | 9169 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4PositiveBusbarInsulationResistanceToGround | {"en":"Cluster 4 positive busbar insulation resistance to ground"}
242 | 簇 4 簇负母线对地绝缘阻值 | U16 | kΩ |  | 9170 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4NegativeBusInsulationResistanceToGround | {"en":"Cluster 4 negative bus insulation resistance to ground"}
243 | 簇 4 簇最大允许放电功率 | U16 | kW |  | 9171 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4MaximumAllowableDischargePower | {"en":"Cluster 4 Maximum allowable discharge power"}
244 | 簇 4 簇最大允许充电功率 | U16 | kW |  | 9172 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4MaximumAllowableChargingPower | {"en":"Cluster 4 Maximum allowable charging power"}
245 | 簇 4 BCMU 软件版本号1 | U16 |  |  | 9173 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4BcmuSoftwareVersion1 | {"en":"Cluster 4 BCMU software version 1"}
246 | 簇 4 BCMU 软件版本号2 | U16 |  |  | 9174 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4BcmuSoftwareVersion2 | {"en":"Cluster 4 BCMU software version 2"}
247 | 簇 4 BCMU 软件版本号3 | U16 |  |  | 9175 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4BcmuSoftwareVersionNumber3 | {"en":"Cluster 4 BCMU software version number 3"}
248 | 簇 4 BCMU 软件版本号4 | U16 |  |  | 9176 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster4BcmuSoftwareVersionNumber4 | {"en":"Cluster 4 BCMU software version number 4"}
249 | 簇 4 包总压压差 | U16 | V |  | 9179 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster4PackageTotalPressureDifference | {"en":"Cluster 4 package total pressure difference"}
250 | 簇 4 簇日放电电量 | U32 | kWh |  | 9181 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster4DailyDischargeElectricity | {"en":"Cluster 4 daily discharge electricity"}
251 | 簇 4 簇日充电电量 | U32 | kWh |  | 9183 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster4DailyChargingCapacity | {"en":"Cluster 4 daily charging capacity"}
252 | 簇 4 簇累计放电电量 | U32 | kWh |  | 9185 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | accumulatedDischargePowerOfCluster4 | {"en":"Accumulated discharge power of cluster 4"}
253 | 簇 4 簇累计充电电量 | U32 | kWh |  | 9187 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster4AccumulatedChargingCapacity | {"en":"Cluster 4 Accumulated Charging Capacity"}
254 | 簇 4 簇可放电量 | U32 | kWh |  | 9189 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster4CanDischargeElectricity | {"en":"Cluster 4 can discharge electricity"}
255 | 簇 4 簇可充电量 | U32 | kWh |  | 9191 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster4RechargeableCapacity | {"en":"Cluster 4 rechargeable capacity"}
256 | 簇 5 电池簇SOC | U16 | % |  | 9193 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster5BatteryClusterSoc | {"en":"Cluster 5 battery cluster SOC"}
257 | 簇 5 电池簇电压 | U16 | V |  | 9194 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster5BatteryClusterVoltage | {"en":"Cluster 5 battery cluster voltage"}
258 | 簇 5 电池簇电流 | I16 | A |  | 9195 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster5BatteryClusterCurrent | {"en":"Cluster 5 battery cluster current"}
259 | 簇 5 电池簇SOH | U16 | % |  | 9196 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster5BatteryClusterSoh | {"en":"Cluster 5 battery cluster SOH"}
260 | 簇 5 簇单体平均电压 | U16 | mV |  | 9197 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5AverageVoltageOfIndividualCells | {"en":"Cluster 5 average voltage of individual cells"}
261 | 簇 5 簇单体平均温度 | U16 | ℃ |  | 9198 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | averageTemperatureOfCluster5Monomers | {"en":"Average temperature of cluster 5 monomers"}
262 | 簇 5 簇最高单体电压 | U16 | mV |  | 9199 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5HighestSingleCellVoltage | {"en":"Cluster 5, highest single cell voltage"}
263 | 簇 5 簇最高单体电压编号 | U16 |  |  | 9200 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5HighestSingleCellVoltageNumber | {"en":"Cluster 5, highest single cell voltage number"}
264 | 簇 5 簇最低单体电压值 | U16 | mV |  | 9201 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5HasTheLowestSingleCellVoltageValue | {"en":"Cluster 5 has the lowest single cell voltage value"}
265 | 簇 5 簇最低单体电压编号 | U16 |  |  | 9202 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5LowestSingleCellVoltageNumber | {"en":"Cluster 5, lowest single cell voltage number"}
266 | 簇 5 簇次高单体电压 | U16 | mV |  | 9203 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5SubHighSingleCellVoltage | {"en":"Cluster 5, sub high single cell voltage"}
267 | 簇 5 簇次高单体电压编号 | U16 |  |  | 9204 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5SecondaryHighCellVoltageNumber | {"en":"Cluster 5, secondary high cell voltage number"}
268 | 簇 5 簇次低单体电压 | U16 | mV |  | 9205 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5ClustersWithLowCellVoltage | {"en":"Cluster 5 clusters with low cell voltage"}
269 | 簇 5 簇次低单体电压编号 | U16 |  |  | 9206 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5ClusterNumberLowCellVoltage | {"en":"Cluster 5, cluster number, low cell voltage"}
270 | 簇 5 簇最高单体温度 | U16 | ℃ |  | 9207 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster5HighestMonomerTemperature | {"en":"Cluster 5, highest monomer temperature"}
271 | 簇 5 簇最高单体温度编号 | U16 |  |  | 9208 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5HighestMonomerTemperatureNumber | {"en":"Cluster 5, highest monomer temperature number"}
272 | 簇 5 簇最低单体温度 | U16 | ℃ |  | 9209 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster5LowestMonomerTemperature | {"en":"Cluster 5 lowest monomer temperature"}
273 | 簇 5 簇最低单体温度编号 | U16 |  |  | 9210 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5LowestMonomerTemperatureNumber | {"en":"Cluster 5 lowest monomer temperature number"}
274 | 簇 5 簇次高单体温度 | U16 | ℃ |  | 9211 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster5SubHighMonomerTemperature | {"en":"Cluster 5, sub high monomer temperature"}
275 | 簇 5 簇次高单体温度编号 | U16 |  |  | 9212 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5SubHighMonomerTemperatureNumber | {"en":"Cluster 5, sub high monomer temperature number"}
276 | 簇 5 簇次低单体温度 | U16 | ℃ |  | 9213 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster5ClustersWithLowMonomerTemperature | {"en":"Cluster 5 clusters with low monomer temperature"}
277 | 簇 5 簇次低单体温度编号 | U16 |  |  | 9214 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5ClusterNumberLowMonomerTemperature | {"en":"Cluster 5, cluster number, low monomer temperature"}
278 | 簇 5 簇内单体电压极差 | U16 | mV |  | 9215 | InputRegisters | 2 | ABCD | 1 | 0 |  | voltageRangeOfIndividualCellsWithinCluster5 | {"en":"Voltage range of individual cells within cluster 5"}
279 | 簇 5 簇内单体温度极差 | U16 | ℃ |  | 9216 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | temperatureRangeOfMonomersWithinCluster5 | {"en":"Temperature range of monomers within cluster 5"}
280 | 簇 5 簇正母线对地绝缘阻值 | U16 | kΩ |  | 9217 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5PositiveBusbarInsulationResistanceToGround | {"en":"Cluster 5 positive busbar insulation resistance to ground"}
281 | 簇 5 簇负母线对地绝缘阻值 | U16 | kΩ |  | 9218 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5NegativeBusInsulationResistanceToGround | {"en":"Cluster 5 negative bus insulation resistance to ground"}
282 | 簇 5 簇最大允许放电功率 | U16 | kW |  | 9219 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5MaximumAllowableDischargePower | {"en":"Cluster 5 Maximum allowable discharge power"}
283 | 簇 5 簇最大允许充电功率 | U16 | kW |  | 9220 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5MaximumAllowableChargingPower | {"en":"Cluster 5 Maximum allowable charging power"}
284 | 簇 5 BCMU 软件版本号1 | U16 |  |  | 9221 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5BcmuSoftwareVersion1 | {"en":"Cluster 5 BCMU software version 1"}
285 | 簇 5 BCMU 软件版本号2 | U16 |  |  | 9222 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5BcmuSoftwareVersion2 | {"en":"Cluster 5 BCMU software version 2"}
286 | 簇 5 BCMU 软件版本号3 | U16 |  |  | 9223 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5BcmuSoftwareVersionNumber3 | {"en":"Cluster 5 BCMU software version number 3"}
287 | 簇 5 BCMU 软件版本号4 | U16 |  |  | 9224 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster5BcmuSoftwareVersionNumber4 | {"en":"Cluster 5 BCMU software version number 4"}
288 | 簇 5 包总压压差 | U16 | V |  | 9227 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster5PackageTotalPressureDifference | {"en":"Cluster 5 package total pressure difference"}
289 | 簇 5 簇日放电电量 | U32 | kWh |  | 9229 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster5DailyDischargeElectricity | {"en":"Cluster 5 daily discharge electricity"}
290 | 簇 5 簇日充电电量 | U32 | kWh |  | 9231 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster5DailyChargingCapacity | {"en":"Cluster 5 daily charging capacity"}
291 | 簇 5 簇累计放电电量 | U32 | kWh |  | 9233 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | accumulatedDischargePowerOfCluster5 | {"en":"Accumulated discharge power of cluster 5"}
292 | 簇 5 簇累计充电电量 | U32 | kWh |  | 9235 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster5AccumulatedChargingCapacity | {"en":"Cluster 5 Accumulated Charging Capacity"}
293 | 簇 5 簇可放电量 | U32 | kWh |  | 9237 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster5CanDischargeElectricity | {"en":"Cluster 5 can discharge electricity"}
294 | 簇 5 簇可充电量 | U32 | kWh |  | 9239 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster5RechargeableCapacity | {"en":"Cluster 5 rechargeable capacity"}
295 | 簇 6 电池簇SOC | U16 | % |  | 9241 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster6BatteryClusterSoc | {"en":"Cluster 6 battery cluster SOC"}
296 | 簇 6 电池簇电压 | U16 | V |  | 9242 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster6BatteryClusterVoltage | {"en":"Cluster 6 battery cluster voltage"}
297 | 簇 6 电池簇电流 | I16 | A |  | 9243 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster6BatteryClusterCurrent | {"en":"Cluster 6 battery cluster current"}
298 | 簇 6 电池簇SOH | U16 | % |  | 9244 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster6BatteryClusterSoh | {"en":"Cluster 6 battery cluster SOH"}
299 | 簇 6 簇单体平均电压 | U16 | mV |  | 9245 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6AverageVoltageOfIndividualCells | {"en":"Cluster 6 average voltage of individual cells"}
300 | 簇 6 簇单体平均温度 | U16 | ℃ |  | 9246 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | averageTemperatureOfCluster6Monomers | {"en":"Average temperature of cluster 6 monomers"}
301 | 簇 6 簇最高单体电压 | U16 | mV |  | 9247 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6HighestSingleCellVoltage | {"en":"Cluster 6, highest single cell voltage"}
302 | 簇 6 簇最高单体电压编号 | U16 |  |  | 9248 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6HighestSingleCellVoltageNumber | {"en":"Cluster 6, highest single cell voltage number"}
303 | 簇 6 簇最低单体电压值 | U16 | mV |  | 9249 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6LowestSingleCellVoltageValue | {"en":"Cluster 6, lowest single cell voltage value"}
304 | 簇 6 簇最低单体电压编号 | U16 |  |  | 9250 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6LowestSingleCellVoltageNumber | {"en":"Cluster 6, lowest single cell voltage number"}
305 | 簇 6 簇次高单体电压 | U16 | mV |  | 9251 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6SubHighSingleCellVoltage | {"en":"Cluster 6, sub high single cell voltage"}
306 | 簇 6 簇次高单体电压编号 | U16 |  |  | 9252 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6SubHighCellVoltageNumber | {"en":"Cluster 6, sub high cell voltage number"}
307 | 簇 6 簇次低单体电压 | U16 | mV |  | 9253 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6ClustersWithLowCellVoltage | {"en":"Cluster 6 clusters with low cell voltage"}
308 | 簇 6 簇次低单体电压编号 | U16 |  |  | 9254 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6Cluster2LowCellVoltageNumber | {"en":"Cluster 6, Cluster 2, Low Cell Voltage Number"}
309 | 簇 6 簇最高单体温度 | U16 | ℃ |  | 9255 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster6HighestMonomerTemperature | {"en":"Cluster 6, highest monomer temperature"}
310 | 簇 6 簇最高单体温度编号 | U16 |  |  | 9256 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6HighestMonomerTemperatureNumber | {"en":"Cluster 6, highest monomer temperature number"}
311 | 簇 6 簇最低单体温度 | U16 | ℃ |  | 9257 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster6LowestMonomerTemperature | {"en":"Cluster 6 lowest monomer temperature"}
312 | 簇 6 簇最低单体温度编号 | U16 |  |  | 9258 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6LowestMonomerTemperatureNumber | {"en":"Cluster 6 lowest monomer temperature number"}
313 | 簇 6 簇次高单体温度 | U16 | ℃ |  | 9259 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster6SubHighMonomerTemperature | {"en":"Cluster 6, sub high monomer temperature"}
314 | 簇 6 簇次高单体温度编号 | U16 |  |  | 9260 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6SubHighMonomerTemperatureNumber | {"en":"Cluster 6, sub high monomer temperature number"}
315 | 簇 6 簇次低单体温度 | U16 | ℃ |  | 9261 | InputRegisters | 2 | ABCD | 0.1 | -40 |  | cluster6ClustersWithLowMonomerTemperature | {"en":"Cluster 6 clusters with low monomer temperature"}
316 | 簇 6 簇次低单体温度编号 | U16 |  |  | 9262 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6ClusterNumberLowMonomerTemperature | {"en":"Cluster 6, cluster number, low monomer temperature"}
317 | 簇 6 簇内单体电压极差 | U16 | mV |  | 9263 | InputRegisters | 2 | ABCD | 1 | 0 |  | voltageRangeOfIndividualCellsWithinCluster6 | {"en":"Voltage range of individual cells within cluster 6"}
318 | 簇 6 簇内单体温度极差 | U16 | ℃ |  | 9264 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | temperatureRangeOfMonomersWithinCluster6 | {"en":"Temperature range of monomers within cluster 6"}
319 | 簇 6 簇正母线对地绝缘阻值 | U16 | kΩ |  | 9265 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6PositiveBusbarInsulationResistanceToGround | {"en":"Cluster 6 positive busbar insulation resistance to ground"}
320 | 簇 6 簇负母线对地绝缘阻值 | U16 | kΩ |  | 9266 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6NegativeBusInsulationResistanceToGround | {"en":"Cluster 6 negative bus insulation resistance to ground"}
321 | 簇 6 簇最大允许放电功率 | U16 | kW |  | 9267 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6MaximumAllowableDischargePower | {"en":"Cluster 6 Maximum allowable discharge power"}
322 | 簇 6 簇最大允许充电功率 | U16 | kW |  | 9268 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6MaximumAllowableChargingPower | {"en":"Cluster 6 Maximum allowable charging power"}
323 | 簇 6 BCMU 软件版本号1 | U16 |  |  | 9269 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6BcmuSoftwareVersion1 | {"en":"Cluster 6 BCMU software version 1"}
324 | 簇 6 BCMU 软件版本号2 | U16 |  |  | 9270 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6BcmuSoftwareVersion2 | {"en":"Cluster 6 BCMU software version 2"}
325 | 簇 6 BCMU 软件版本号3 | U16 |  |  | 9271 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6BcmuSoftwareVersionNumber3 | {"en":"Cluster 6 BCMU software version number 3"}
326 | 簇 6 BCMU 软件版本号4 | U16 |  |  | 9272 | InputRegisters | 2 | ABCD | 1 | 0 |  | cluster6BcmuSoftwareVersionNumber4 | {"en":"Cluster 6 BCMU software version number 4"}
327 | 簇 6 包总压压差 | U16 | V |  | 9275 | InputRegisters | 2 | ABCD | 0.1 | 0 |  | cluster6PackageTotalPressureDifference | {"en":"Cluster 6 package total pressure difference"}
328 | 簇 6 簇日放电电量 | U32 | kWh |  | 9277 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster6DailyDischargeElectricity | {"en":"Cluster 6 daily discharge electricity"}
329 | 簇 6 簇日充电电量 | U32 | kWh |  | 9279 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster6DailyChargingCapacity | {"en":"Cluster 6 daily charging capacity"}
330 | 簇 6 簇累计放电电量 | U32 | kWh |  | 9281 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | accumulatedDischargePowerOfCluster6 | {"en":"Accumulated discharge power of cluster 6"}
331 | 簇 6 簇累计充电电量 | U32 | kWh |  | 9283 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster6AccumulatedChargingCapacity | {"en":"Cluster 6 Accumulated Charging Capacity"}
332 | 簇 6 簇可放电量 | U32 | kWh |  | 9285 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster6CanDischargeElectricity | {"en":"Cluster 6 can discharge electricity"}
333 | 簇 6 簇可充电量 | U32 | kWh |  | 9287 | InputRegisters | 4 | ABCD | 0.1 | 0 |  | cluster6RechargeableCapacity | {"en":"Cluster 6 rechargeable capacity"}
500 | 簇 1 单体电压 | U16 | mV |  | 11001 | InputRegisters | 416 | ABCD | 1 | 0 |  | cluster1MonomerVoltage | {"en":"Cluster 1 monomer voltage"}
501 | 簇 2 单体电压 | U16 | mV |  | 11417 | InputRegisters | 416 | ABCD | 1 | 0 |  | cluster2MonomerVoltage | {"en":"Cluster 2 monomer voltage"}
502 | 簇 3 单体电压 | U16 | mV |  | 11833 | InputRegisters | 416 | ABCD | 1 | 0 |  | cluster3MonomerVoltage | {"en":"Cluster 3 monomer voltage"}
503 | 簇 4 单体电压 | U16 | mV |  | 12249 | InputRegisters | 416 | ABCD | 1 | 0 |  | cluster4MonomerVoltage | {"en":"Cluster 4 monomer voltage"}
504 | 簇 5 单体电压 | U16 | mV |  | 12665 | InputRegisters | 416 | ABCD | 1 | 0 |  | cluster5MonomerVoltage | {"en":"Cluster 5 monomer voltage"}
505 | 簇 6 单体电压 | U16 | mV |  | 13081 | InputRegisters | 416 | ABCD | 1 | 0 |  | cluster6MonomerVoltage | {"en":"Cluster 6 monomer voltage"}
506 | 簇 1 单体温度 | U16 | °C |  | 30001 | InputRegisters | 208 | ABCD | 0.1 | -40 |  | cluster1MonomerTemperature | {"en":"Cluster 1 monomer temperature"}
507 | 簇 2 单体温度 | U16 | °C |  | 30209 | InputRegisters | 208 | ABCD | 0.1 | -40 |  | cluster2MonomerTemperature | {"en":"Cluster 2 monomer temperature"}
508 | 簇 3 单体温度 | U16 | °C |  | 30417 | InputRegisters | 208 | ABCD | 0.1 | -40 |  | cluster3MonomerTemperature | {"en":"Cluster 3 monomer temperature"}
509 | 簇 4 单体温度 | U16 | °C |  | 30625 | InputRegisters | 208 | ABCD | 0.1 | -40 |  | cluster4MonomerTemperature | {"en":"Cluster 4 monomer temperature"}
510 | 簇 5 单体温度 | U16 | °C |  | 30833 | InputRegisters | 208 | ABCD | 0.1 | -40 |  | cluster5MonomerTemperature | {"en":"Cluster 5 monomer temperature"}
511 | 簇 6 单体温度 | U16 | °C |  | 31041 | InputRegisters | 208 | ABCD | 0.1 | -40 |  | cluster6MonomerTemperature | {"en":"Cluster 6 monomer temperature"}
600 | 消防系统故障状态 | U16 |  | 0：正常 1：消防系统故障 | 45002 | InputRegisters | 2 | ABCD | 1 | 0 |  | fireProtectionSystemMalfunctionStatus | {"en":"Fire protection system malfunction status"}
601 | 消防火警一级故障 | U16 |  | 0：正常 1：火警三级故障 | 45003 | InputRegisters | 2 | ABCD | 1 | 0 |  | fireAlarmLevelOneMalfunction | {"en":"Fire alarm level one malfunction"}
602 | 消防火警三级预警 | U16 |  | 0：正常 1：火警一级预警 | 45005 | InputRegisters | 2 | ABCD | 1 | 0 |  | level3FireAlarmWarning | {"en":"Level 3 Fire Alarm Warning"}
603 | 液冷机通讯状态 | U16 |  | 0：正常 1：通讯异常 | 45006 | InputRegisters | 2 | ABCD | 1 | 0 |  | communicationStatusOfLiquidCooler | {"en":"Communication status of liquid cooler"}
604 | 液冷机运行状态 | U16 |  | 0：停机 1：运行 | 45007 | InputRegisters | 2 | ABCD | 1 | 0 |  | operationStatusOfLiquidCooler | {"en":"Operation status of liquid cooler"}
605 | 液冷机循环水泵 | U16 |  | 0：关闭 1：开启 | 45008 | InputRegisters | 2 | ABCD | 1 | 0 |  | liquidCooledCirculatingWaterPump | {"en":"Liquid cooled circulating water pump"}
606 | 液冷机压缩机 | U16 |  | 0：关闭 1：开启 | 45009 | InputRegisters | 2 | ABCD | 1 | 0 |  | liquidCooledCompressor | {"en":"Liquid cooled compressor"}
607 | 液冷机电加热 | U16 |  | 0：关闭 1：开启 | 45010 | InputRegisters | 2 | ABCD | 1 | 0 |  | liquidCooledElectromechanicalHeating | {"en":"Liquid cooled electromechanical heating"}
608 | 液冷机故障状态 | U16 |  | 0：正常 1：三级故障 | 45011 | InputRegisters | 2 | ABCD | 1 | 0 |  | faultStatusOfLiquidCoolingMachine | {"en":"Fault status of liquid cooling machine"}
609 | 液冷机出水口温度值 | U16 |  |  | 45012 | InputRegisters | 2 | ABCD | 1 | 0 |  | temperatureValueAtTheOutletOfTheLiquidCooler | {"en":"Temperature value at the outlet of the liquid cooler"}
610 | 液冷机工作状态 | U16 |  | 0：自动模式 1：制冷模式 2：制热模式 3：泵循环模式 4：待机模式 | 45015 | InputRegisters | 2 | ABCD | 1 | 0 |  | workingStatusOfLiquidCoolingMachine | {"en":"Working status of liquid cooling machine"}
611 | 空调通讯状态 | U16 |  | 0：正常 1：通讯异常 | 45016 | InputRegisters | 2 | ABCD | 1 | 0 |  | airConditioningCommunicationStatus | {"en":"Air conditioning communication status"}
612 | 空调整机运行状态 | U16 |  | 0：停机 1：运行 | 45017 | InputRegisters | 2 | ABCD | 1 | 0 |  | operatingStatusOfTheEntireAirConditioningSystem | {"en":"Operating status of the entire air conditioning system"}
613 | 空调压缩机（制冷） | U16 |  | 0：关闭 1：开启 | 45018 | InputRegisters | 2 | ABCD | 1 | 0 |  | airConditioningCompressorRefrigeration | {"en":"Air conditioning compressor (refrigeration)"}
614 | 空调电加热（制热） | U16 |  | 0：关闭 1：开启 | 45019 | InputRegisters | 2 | ABCD | 1 | 0 |  | airConditioningElectricHeatingHeating | {"en":"Air conditioning electric heating (heating)"}
615 | 空调故障状态 | U16 |  | 0：正常 1：故障 | 45020 | InputRegisters | 2 | ABCD | 1 | 0 |  | airConditioningMalfunctionStatus | {"en":"Air conditioning malfunction status"}
616 | 温度值 | U16 |  |  | 45021 | InputRegisters | 2 | ABCD | 1 | 0 |  | temperatureValue | {"en":"temperature value"}
617 | 空调工作模式 | U16 |  | 0：自动模式 1：制冷模式 2：制热模式 3：送风模式 4：待机模式 | 45024 | InputRegisters | 2 | ABCD | 1 | 0 |  | airConditioningWorkingMode | {"en":"Air conditioning working mode"}

## 遥调
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位
2000 | 系统开关机 | U16 |  | 0：关机 1：开机 | 0 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | systemPowerOnOff | {"en":"System power on/off"}
2001 | 软件急停 | U16 |  | 0：无操作 1：EMS急停 | 1 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | softwareEmergencyStop | {"en":"Software emergency stop"}
2002 | 故障复归 | U16 |  | 0：无操作 1：故障复归 | 2 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | faultReset | {"en":"Fault reset"}
2003 | 接触器控制（预留） | U16 |  | 0：一键断开 1：一键闭合 | 3 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | contactorControlReserved | {"en":"Contactor control (reserved)"}
2004 | 主隔离开关分合闸控制(预留) | U16 |  | 0：分闸 1：合闸 | 4 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | mainIsolationSwitchOnOffControlReserved | {"en":"Main isolation switch on/off control (reserved)"}
2005 | 工作模式控制 | U16 |  | 0-正常模式 1-缺簇模式 | 5 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | workModeControl | {"en":"Work mode control"}
2006 | 簇 1 启停 | U16 |  | 0-停用 1-启用 | 6 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | cluster1StartStop | {"en":"Cluster 1 start stop"}
2007 | 簇 2 启停 | U16 |  |  | 7 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | cluster2StartStop | {"en":"Cluster 2 start stop"}
2008 | 簇 3 启停 | U16 |  |  | 8 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | cluster3StartStop | {"en":"Cluster 3 start stop"}
2009 | 簇 4 启停 | U16 |  |  | 9 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | cluster4StartStop | {"en":"Cluster 4 start stop"}
2010 | 簇 5 启停 | U16 |  |  | 10 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | cluster5StartStop | {"en":"Cluster 5 start stop"}
2011 | 簇 6 启停 | U16 |  |  | 11 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | cluster6StartStop | {"en":"Cluster 6 start stop"}
2012 | EMS校时（年） | U16 |  |  | 18 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | emsSchoolTimeYear | {"en":"EMS school time (year)"}
2013 | EMS校时（月） | U16 |  |  | 19 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | emsSchoolHoursMonths | {"en":"EMS school hours (months)"}
2014 | EMS校时（日） | U16 |  |  | 20 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | emsSchoolTimeDay | {"en":"EMS school time (day)"}
2015 | EMS校时（时） | U16 |  |  | 21 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | emsSchoolTimeHour | {"en":"EMS school time (hour)"}
2016 | EMS校时（分） | U16 |  |  | 22 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | emsSchoolHoursMinutes | {"en":"EMS school hours (minutes)"}
2017 | EMS校时（秒） | U16 |  |  | 23 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | emsCalibrationTimeSeconds | {"en":"EMS calibration time (seconds)"}
2018 | EMS/EMU看门狗 | U16 |  | 0~65535依次递增 | 24 | HoldingRegisters | 2 | ABCD | 1 | 0 |  | emsEmuWatchdog | {"en":"EMS/EMU watchdog"}

## 遥信
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位
1000 | 堆开关机状态 | bool |  | 0：关机 1：开机 | 201 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileOnOffStatus | {"en":"Pile on/off status"}
1001 | 堆运维状态 | bool |  | 0：运维功能关闭 1：运维功能开启 | 202 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileOperationAndMaintenanceStatus | {"en":"Pile operation and maintenance status"}
1002 | 堆就地/远方模式 | bool |  | 0：就地 1：远方 | 203 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileOnSiteRemoteMode | {"en":"Pile on site/remote mode"}
1003 | 堆工作模式 | bool |  | 0：正常运行 1：缺簇模式 | 204 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileWorkingMode | {"en":"Pile working mode"}
1004 | 堆启用/停用状态 | bool |  | 0：停用 1：启用 | 205 | DiscreteInputs | 1 | AB | 1 | 0 |  | heapEnabledDisabledStatus | {"en":"Heap enabled/disabled status"}
1005 | 堆充电状态 | bool |  | 0：空闲 1：充电 | 206 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileChargingStatus | {"en":"Pile charging status"}
1006 | 堆放电状态 | bool |  | 0：空闲 1：放电 | 207 | DiscreteInputs | 1 | AB | 1 | 0 |  | stackedElectricalStatus | {"en":"Stacked electrical status"}
1007 | 堆一级故障 | bool |  | 0：系统正常 1：三级故障 | 208 | DiscreteInputs | 1 | AB | 1 | 0 |  | level1FaultInTheReactor | {"en":"Level 1 fault in the reactor"}
1008 | 堆二级告警 | bool |  | 0：系统正常 1：二级告警 | 209 | DiscreteInputs | 1 | AB | 1 | 0 |  | level2ReactorAlarm | {"en":"Level 2 reactor alarm"}
1009 | 堆三级预警 | bool |  | 0：系统正常 1：一级预警 | 210 | DiscreteInputs | 1 | AB | 1 | 0 |  | level3WarningForPiles | {"en":"Level 3 warning for piles"}
1010 | 堆禁充标志 | bool |  | 0：允许 1：禁止充电 | 211 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileProhibitionMark | {"en":"Pile prohibition mark"}
1011 | 堆禁放标志 | bool |  | 0：允许 1：禁止放电 | 212 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileProhibitionSign | {"en":"Pile prohibition sign"}
1012 | 与PCS通讯状态 | bool |  | 0：正常 1：通讯异常（三级故障） | 213 | DiscreteInputs | 1 | AB | 1 | 0 |  | communicationStatusWithPcs | {"en":"Communication status with PCS"}
1013 | 与EMS通讯状态 | bool |  | 0：正常 1：通讯异常（三级故障） | 214 | DiscreteInputs | 1 | AB | 1 | 0 |  | communicationStatusWithEms | {"en":"Communication status with EMS"}
1014 | 主隔离开关状态 | bool |  | 0：分闸 1：合闸 | 215 | DiscreteInputs | 1 | AB | 1 | 0 |  | mainIsolationSwitchStatus | {"en":"Main isolation switch status"}
1015 | 硬件急停 | bool |  | 0：正常 1：急停输入（三级故障） | 216 | DiscreteInputs | 1 | AB | 1 | 0 |  | hardwareEmergencyStop | {"en":"Hardware emergency stop"}
1016 | 主隔离开关合闸回路 | bool |  | 0：未使能（未控制合闸） 1：使能（控制合闸） | 217 | DiscreteInputs | 1 | AB | 1 | 0 |  | mainIsolationSwitchClosingCircuit | {"en":"Main isolation switch closing circuit"}
1017 | 主隔离开关分闸回路 | bool |  | 0：未使能（未控制分闸） 1：使能（控制分闸） | 218 | DiscreteInputs | 1 | AB | 1 | 0 |  | mainIsolationSwitchOpeningCircuit | {"en":"Main isolation switch opening circuit"}
1018 | PCS急停控制干接点 | bool |  | 0：未使能（未控制停机） 1：使能（控制停机） | 219 | DiscreteInputs | 1 | AB | 1 | 0 |  | pcsEmergencyStopControlDryContact | {"en":"PCS emergency stop control dry contact"}
1019 | 高压箱断路器/隔离开关总状态 | bool |  | 0：断开（断开） 1：闭合 （启用簇全部闭合） | 220 | DiscreteInputs | 1 | AB | 1 | 0 |  | generalStatusOfHighVoltageBoxCircuitBreakerIsolatingSwitch | {"en":"General status of high-voltage box circuit breaker/isolating switch"}
1020 | 接触器总状态 | bool |  | 0：断开（断开） 1：闭合（启用簇全部闭合） | 221 | DiscreteInputs | 1 | AB | 1 | 0 |  | overallStatusOfContactor | {"en":"Overall status of contactor"}
1021 | 总正接触器粘连 | bool |  | 0：正常 1：三级故障 | 222 | DiscreteInputs | 1 | AB | 1 | 0 |  | adhesionOfTheMainPositiveContactor | {"en":"Adhesion of the main positive contactor"}
1022 | 总负接触器粘连 | bool |  | 0：正常 1：三级故障 | 223 | DiscreteInputs | 1 | AB | 1 | 0 |  | totalNegativeContactorAdhesion | {"en":"Total negative contactor adhesion"}
1023 | 总正接触器卡滞 | bool |  | 0：正常 1：三级故障 | 225 | DiscreteInputs | 1 | AB | 1 | 0 |  | theMainPositiveContactorIsStuck | {"en":"The main positive contactor is stuck"}
1024 | 总负接触器卡滞 | bool |  | 0：正常 1：三级故障 | 226 | DiscreteInputs | 1 | AB | 1 | 0 |  | theTotalNegativeContactorIsStuck | {"en":"The total negative contactor is stuck"}
1025 | 单体电压采集故障 | bool |  | 0：正常 1：三级故障 | 228 | DiscreteInputs | 1 | AB | 1 | 0 |  | singleCellVoltageAcquisitionFault | {"en":"Single cell voltage acquisition fault"}
1026 | 单体温度采集故障 | bool |  | 0：正常 1：三级故障 | 229 | DiscreteInputs | 1 | AB | 1 | 0 |  | individualTemperatureAcquisitionFault | {"en":"Individual temperature acquisition fault"}
1027 | INCAN接收异常 | bool |  | 0：正常 1：三级故障 | 231 | DiscreteInputs | 1 | AB | 1 | 0 |  | incanReceivingException | {"en":"INCAN receiving exception"}
1028 | BMU通讯故障 | bool |  | 0：正常 1：三级故障 | 232 | DiscreteInputs | 1 | AB | 1 | 0 |  | bmuCommunicationFailure | {"en":"BMU communication failure"}
1029 | BCMU通讯故障 | bool |  | 0：正常 1：三级故障 | 233 | DiscreteInputs | 1 | AB | 1 | 0 |  | bcmuCommunicationFailure | {"en":"BCMU communication failure"}
1030 | BAMU通讯故障 | bool |  | 0：正常 1：三级故障 | 234 | DiscreteInputs | 1 | AB | 1 | 0 |  | bamuCommunicationFailure | {"en":"BAMU communication failure"}
1031 | 充电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 236 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitOvervoltageLevelOneFault | {"en":"Charging unit overvoltage level one fault"}
1032 | 放电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 237 | DiscreteInputs | 1 | AB | 1 | 0 |  | dischargeUnitOvervoltageLevelOneFault | {"en":"Discharge unit overvoltage level one fault"}
1033 | 充电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 238 | DiscreteInputs | 1 | AB | 1 | 0 |  | level1UndervoltageFaultOfChargingUnit | {"en":"Level 1 undervoltage fault of charging unit"}
1034 | 放电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 239 | DiscreteInputs | 1 | AB | 1 | 0 |  | underVoltagePrimaryFaultOfDischargeCell | {"en":"Under voltage primary fault of discharge cell"}
1035 | 充电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 240 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitVoltageDifferenceIsTooLargeLevelOneFault | {"en":"Charging unit voltage difference is too large, level one fault"}
1036 | 放电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 241 | DiscreteInputs | 1 | AB | 1 | 0 |  | primaryFaultOfExcessiveVoltageDifferenceInDischargeCell | {"en":"Primary fault of excessive voltage difference in discharge cell"}
1037 | 充电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 242 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingClusterTotalVoltageTooHighLevelOneFault | {"en":"Charging cluster total voltage too high level one fault"}
1038 | 放电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 243 | DiscreteInputs | 1 | AB | 1 | 0 |  | dischargeClusterTotalVoltageTooHighLevelOneFault | {"en":"Discharge cluster total voltage too high level one fault"}
1039 | 充电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 244 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingClusterTotalVoltageTooLowLevelOneFault | {"en":"Charging cluster total voltage too low level one fault"}
1040 | 放电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 245 | DiscreteInputs | 1 | AB | 1 | 0 |  | dischargeClusterTotalVoltageTooLowLevelOneFault | {"en":"Discharge cluster total voltage too low level one fault"}
1041 | 充电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 246 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitHighTemperatureLevelOneFault | {"en":"Charging unit high temperature level one fault"}
1042 | 放电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 247 | DiscreteInputs | 1 | AB | 1 | 0 |  | highTemperaturePrimaryFaultOfDischargeUnit | {"en":"High temperature primary fault of discharge unit"}
1043 | 充电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 248 | DiscreteInputs | 1 | AB | 1 | 0 |  | lowTemperaturePrimaryFaultOfChargingUnit | {"en":"Low temperature primary fault of charging unit"}
1044 | 放电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 249 | DiscreteInputs | 1 | AB | 1 | 0 |  | lowTemperaturePrimaryFaultOfDischargeCell | {"en":"Low temperature primary fault of discharge cell"}
1045 | 充电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 250 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitTemperatureDifferenceIsTooLargeLevelOneFault | {"en":"Charging unit temperature difference is too large, level one fault"}
1046 | 放电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 251 | DiscreteInputs | 1 | AB | 1 | 0 |  | level1FaultOfExcessiveTemperatureDifferenceInDischargeUnit | {"en":"Level 1 fault of excessive temperature difference in discharge unit"}
1047 | 充电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 252 | DiscreteInputs | 1 | AB | 1 | 0 |  | level1FaultOfExcessiveTotalVoltageDifferenceInTheChargingCompartment | {"en":"Level 1 fault of excessive total voltage difference in the charging compartment"}
1048 | 放电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 253 | DiscreteInputs | 1 | AB | 1 | 0 |  | firstLevelFaultOfExcessiveTotalPressureDifferenceBetweenDischargeCompartments | {"en":"First level fault of excessive total pressure difference between discharge compartments"}
1049 | 充电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 254 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingBagTotalVoltageTooHighLevelOneFault | {"en":"Charging bag total voltage too high level one fault"}
1050 | 放电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 255 | DiscreteInputs | 1 | AB | 1 | 0 |  | firstLevelFaultOfHighTotalVoltageOfDischargePack | {"en":"First level fault of high total voltage of discharge pack"}
1051 | 充电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 256 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingBagTotalVoltageTooLowLevelOneFault | {"en":"Charging bag total voltage too low level one fault"}
1052 | 放电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 257 | DiscreteInputs | 1 | AB | 1 | 0 |  | dischargePackTotalPressureTooLowLevelOneFault | {"en":"Discharge pack total pressure too low level one fault"}
1053 | 充电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 258 | DiscreteInputs | 1 | AB | 1 | 0 |  | level1FaultDueToExcessiveChargingCurrent | {"en":"Level 1 fault due to excessive charging current"}
1054 | 放电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 259 | DiscreteInputs | 1 | AB | 1 | 0 |  | firstLevelFaultDueToExcessiveDischargeCurrent | {"en":"First level fault due to excessive discharge current"}
1055 | 绝缘过低一级故障 | bool |  | 0：正常 1：三级故障 | 260 | DiscreteInputs | 1 | AB | 1 | 0 |  | lowInsulationLevelOneFault | {"en":"Low insulation level one fault"}
1056 | SOC过低一级故障 | bool |  | 0：正常 1：三级故障 | 262 | DiscreteInputs | 1 | AB | 1 | 0 |  | socLevelOneLowFault | {"en":"SOC level one low fault"}
1057 | 热失控故障 | bool |  | 0：正常 1：三级故障 | 263 | DiscreteInputs | 1 | AB | 1 | 0 |  | thermalRunawayFailure | {"en":"thermal runaway failure"}
1058 | 电流采集故障 | bool |  | 0：正常 1：三级故障 | 264 | DiscreteInputs | 1 | AB | 1 | 0 |  | currentCollectionFault | {"en":"Current collection fault"}
1059 | 簇内压差过大故障 | bool |  | 0：正常 1：三级故障 | 265 | DiscreteInputs | 1 | AB | 1 | 0 |  | faultOfExcessivePressureDifferenceWithinTheCluster | {"en":"Fault of excessive pressure difference within the cluster"}
1060 | 簇间压差过大故障 | bool |  | 0：正常 1：三级故障 | 266 | DiscreteInputs | 1 | AB | 1 | 0 |  | faultOfExcessivePressureDifferenceBetweenClusters | {"en":"Fault of excessive pressure difference between clusters"}
1061 | 管路漏液故障（三级BMS检测） | bool |  | 0：正常 1：三级故障 | 267 | DiscreteInputs | 1 | AB | 1 | 0 |  | pipelineLeakageFaultLevel3BmsDetection | {"en":"Pipeline leakage fault (Level 3 BMS detection)"}
1062 | 充电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 272 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitOvervoltageLevel2Alarm | {"en":"Charging unit overvoltage level 2 alarm"}
1063 | 放电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 273 | DiscreteInputs | 1 | AB | 1 | 0 |  | dischargeCellOvervoltageLevel2Alarm | {"en":"Discharge cell overvoltage level 2 alarm"}
1064 | 充电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 274 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitUndervoltageLevel2Alarm | {"en":"Charging unit undervoltage level 2 alarm"}
1065 | 放电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 275 | DiscreteInputs | 1 | AB | 1 | 0 |  | dischargeCellUndervoltageLevel2Alarm | {"en":"Discharge cell undervoltage level 2 alarm"}
1066 | 充电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 276 | DiscreteInputs | 1 | AB | 1 | 0 |  | level2AlarmForExcessiveVoltageDifferenceInChargingUnit | {"en":"Level 2 alarm for excessive voltage difference in charging unit"}
1067 | 放电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 277 | DiscreteInputs | 1 | AB | 1 | 0 |  | level2AlarmForExcessiveDischargeCellPressureDifference | {"en":"Level 2 alarm for excessive discharge cell pressure difference"}
1068 | 充电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 278 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingClusterTotalVoltageOverLevel2Alarm | {"en":"Charging cluster total voltage over level 2 alarm"}
1069 | 放电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 279 | DiscreteInputs | 1 | AB | 1 | 0 |  | highLevel2AlarmForTotalVoltageExceedingDischargeCluster | {"en":"High Level 2 Alarm for Total Voltage Exceeding Discharge Cluster"}
1070 | 充电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 280 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForLowTotalVoltageOfChargingCluster | {"en":"Secondary alarm for low total voltage of charging cluster"}
1071 | 放电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 281 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForLowTotalVoltageOfDischargeCluster | {"en":"Secondary alarm for low total voltage of discharge cluster"}
1072 | 充电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 282 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitHighTemperatureLevel2Alarm | {"en":"Charging unit high temperature level 2 alarm"}
1073 | 放电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 283 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryHighTemperatureAlarmForDischargeUnit | {"en":"Secondary high temperature alarm for discharge unit"}
1074 | 充电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 284 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitLowTemperatureLevel2Alarm | {"en":"Charging unit low temperature level 2 alarm"}
1075 | 放电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 285 | DiscreteInputs | 1 | AB | 1 | 0 |  | dischargeCellLowTemperatureLevel2Alarm | {"en":"Discharge cell low temperature level 2 alarm"}
1076 | 充电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 286 | DiscreteInputs | 1 | AB | 1 | 0 |  | level2AlarmForExcessiveTemperatureDifferenceOnTheChargingUnit | {"en":"Level 2 alarm for excessive temperature difference on the charging unit"}
1077 | 放电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 287 | DiscreteInputs | 1 | AB | 1 | 0 |  | level2AlarmForExcessiveTemperatureDifferenceInDischargeUnit | {"en":"Level 2 alarm for excessive temperature difference in discharge unit"}
1078 | 充电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 288 | DiscreteInputs | 1 | AB | 1 | 0 |  | level2AlarmForExcessiveTotalVoltageDifferenceInTheChargingCompartment | {"en":"Level 2 alarm for excessive total voltage difference in the charging compartment"}
1079 | 放电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 289 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForExcessiveTotalPressureDifferenceBetweenDischargeCompartments | {"en":"Secondary alarm for excessive total pressure difference between discharge compartments"}
1080 | 充电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 290 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingBagTotalVoltageExceedsLevel2Alarm | {"en":"Charging bag total voltage exceeds level 2 alarm"}
1081 | 放电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 291 | DiscreteInputs | 1 | AB | 1 | 0 |  | highLevel2AlarmForTotalVoltageExceedingDischargePackage | {"en":"High Level 2 Alarm for Total Voltage Exceeding Discharge Package"}
1082 | 充电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 292 | DiscreteInputs | 1 | AB | 1 | 0 |  | level2AlarmForLowTotalVoltageOfChargingBag | {"en":"Level 2 alarm for low total voltage of charging bag"}
1083 | 放电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 293 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForLowTotalVoltageOfDischargePack | {"en":"Secondary alarm for low total voltage of discharge pack"}
1084 | 充电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 294 | DiscreteInputs | 1 | AB | 1 | 0 |  | level2AlarmForExcessiveChargingCurrent | {"en":"Level 2 alarm for excessive charging current"}
1085 | 放电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 295 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForExcessiveDischargeCurrent | {"en":"Secondary alarm for excessive discharge current"}
1086 | 绝缘过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 296 | DiscreteInputs | 1 | AB | 1 | 0 |  | lowInsulationLevel2Alarm | {"en":"Low insulation level 2 alarm"}
1087 | SOC过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 298 | DiscreteInputs | 1 | AB | 1 | 0 |  | socLowLevel2Alarm | {"en":"SOC low level 2 alarm"}
1088 | 充电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 299 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitOvervoltageLevelThreeWarning | {"en":"Charging unit overvoltage level three warning"}
1089 | 放电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 300 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelOvervoltageWarningForDischargeCells | {"en":"Three level overvoltage warning for discharge cells"}
1090 | 充电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 301 | DiscreteInputs | 1 | AB | 1 | 0 |  | level3UndervoltageWarningForChargingUnits | {"en":"Level 3 undervoltage warning for charging units"}
1091 | 放电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 302 | DiscreteInputs | 1 | AB | 1 | 0 |  | level3UndervoltageWarningForDischargeCells | {"en":"Level 3 undervoltage warning for discharge cells"}
1092 | 充电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 303 | DiscreteInputs | 1 | AB | 1 | 0 |  | level3WarningForExcessiveVoltageDifferenceInChargingUnit | {"en":"Level 3 warning for excessive voltage difference in charging unit"}
1093 | 放电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 304 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForExcessiveDischargeCellPressureDifference | {"en":"Three level warning for excessive discharge cell pressure difference"}
1094 | 充电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 305 | DiscreteInputs | 1 | AB | 1 | 0 |  | highLevelWarningForChargingClusterTotalVoltageExceedingThreeLevels | {"en":"High level warning for charging cluster total voltage exceeding three levels"}
1095 | 放电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 306 | DiscreteInputs | 1 | AB | 1 | 0 |  | highLevelWarningForDischargeClusterTotalPressureExceedingThreeLevels | {"en":"High level warning for discharge cluster total pressure exceeding three levels"}
1096 | 充电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 307 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForLowTotalVoltageOfChargingCluster | {"en":"Three level warning for low total voltage of charging cluster"}
1097 | 放电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 308 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForLowTotalVoltageOfDischargeCluster | {"en":"Three level warning for low total voltage of discharge cluster"}
1098 | 充电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 309 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitHighTemperatureLevelThreeWarning | {"en":"Charging unit high temperature level three warning"}
1099 | 放电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 310 | DiscreteInputs | 1 | AB | 1 | 0 |  | level3HighTemperatureWarningForDischargeCells | {"en":"Level 3 high temperature warning for discharge cells"}
1100 | 充电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 311 | DiscreteInputs | 1 | AB | 1 | 0 |  | chargingUnitLowTemperatureLevelThreeWarning | {"en":"Charging unit low temperature level three warning"}
1101 | 放电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 312 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelLowTemperatureWarningForDischargeCells | {"en":"Three level low temperature warning for discharge cells"}
1102 | 充电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 313 | DiscreteInputs | 1 | AB | 1 | 0 |  | level3WarningForExcessiveTemperatureDifferenceOnTheChargingUnit | {"en":"Level 3 warning for excessive temperature difference on the charging unit"}
1103 | 放电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 314 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForExcessiveTemperatureDifferenceInDischargeUnit | {"en":"Three level warning for excessive temperature difference in discharge unit"}
1104 | 充电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 315 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForExcessiveTotalVoltageDifferenceInTheChargingCompartment | {"en":"Three level warning for excessive total voltage difference in the charging compartment"}
1105 | 放电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 316 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForExcessiveTotalPressureDifferenceBetweenDischargeCompartments | {"en":"Three level warning for excessive total pressure difference between discharge compartments"}
1106 | 充电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 317 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForHighTotalVoltageOfChargingBag | {"en":"Three level warning for high total voltage of charging bag"}
1107 | 放电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 318 | DiscreteInputs | 1 | AB | 1 | 0 |  | highLevelThreeWarningForTotalVoltageExceedingDischargePackage | {"en":"High Level Three Warning for Total Voltage Exceeding Discharge Package"}
1108 | 充电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 319 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForLowTotalVoltageOfChargingBag | {"en":"Three level warning for low total voltage of charging bag"}
1109 | 放电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 320 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForLowTotalVoltageOfDischargePack | {"en":"Three level warning for low total voltage of discharge pack"}
1110 | 充电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 321 | DiscreteInputs | 1 | AB | 1 | 0 |  | level3WarningForExcessiveChargingCurrent | {"en":"Level 3 warning for excessive charging current"}
1111 | 放电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 322 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForExcessiveDischargeCurrent | {"en":"Three level warning for excessive discharge current"}
1112 | 绝缘过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 323 | DiscreteInputs | 1 | AB | 1 | 0 |  | level3LowInsulationWarning | {"en":"Level 3 low insulation warning"}
1113 | SOC过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 325 | DiscreteInputs | 1 | AB | 1 | 0 |  | socLowLevelThreeWarning | {"en":"SOC low level three warning"}
1114 | 温升告警 | bool |  | 0：系统正常 1：一级预警 | 326 | DiscreteInputs | 1 | AB | 1 | 0 |  | temperatureRiseAlarm | {"en":"Temperature rise alarm"}
1115 | BCMU序列号异常预警 | bool |  | 0：系统正常 1：一级预警 | 327 | DiscreteInputs | 1 | AB | 1 | 0 |  | bcmuSerialNumberAbnormalWarning | {"en":"BCMU serial number abnormal warning"}
1116 | 簇间压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 328 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForExcessiveInterClusterPressureDifference | {"en":"Three level warning for excessive inter cluster pressure difference"}
1117 | 二级SD卡异常 | bool |  | 0：系统正常 1：一级预警 | 329 | DiscreteInputs | 1 | AB | 1 | 0 |  | abnormalSecondarySdCard | {"en":"Abnormal secondary SD card"}
1118 | 电磁阀控制模块通讯状态 | bool |  | 0：系统正常 1：一级预警 | 330 | DiscreteInputs | 1 | AB | 1 | 0 |  | communicationStatusOfSolenoidValveControlModule | {"en":"Communication status of solenoid valve control module"}
1119 | 系统故障下电 | bool |  | 0：正常 1：三级故障 | 331 | DiscreteInputs | 1 | AB | 1 | 0 |  | powerOffDueToSystemMalfunction | {"en":"Power off due to system malfunction"}
1120 | BCMU校时反馈 | bool |  | 0：正常 1：已校时 | 332 | DiscreteInputs | 1 | AB | 1 | 0 |  | bcmuTimingFeedback | {"en":"BCMU timing feedback"}
1121 | 堆联动故障 | bool |  | 0：正常 1：三级故障 | 333 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileLinkageFailure | {"en":"Pile linkage failure"}
1122 | 堆联动故障-急停 | bool |  | 0：正常 1：三级故障 | 334 | DiscreteInputs | 1 | AB | 1 | 0 |  | reactorLinkageFailureEmergencyStop | {"en":"Reactor linkage failure - emergency stop"}
1123 | 堆联动故障-火警 | bool |  | 0：正常 1：三级故障 | 335 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileLinkageFailureFireAlarm | {"en":"Pile linkage failure - fire alarm"}
1124 | 堆联动故障-单体过温一级故障 | bool |  | 0：正常 1：三级故障 | 336 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileLinkageFaultSingleUnitOverheatingLevelOneFault | {"en":"Pile linkage fault - single unit overheating level one fault"}
1125 | 堆联动故障-热失控 | bool |  | 0：正常 1：三级故障 | 337 | DiscreteInputs | 1 | AB | 1 | 0 |  | reactorLinkageFailureThermalRunaway | {"en":"Reactor linkage failure - thermal runaway"}
1126 | 堆联动故障-管路漏液 | bool |  | 0：正常 1：三级故障 | 338 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileLinkageFailurePipelineLeakage | {"en":"Pile linkage failure - pipeline leakage"}
1127 | 堆联动故障-浪涌脱扣故障 | bool |  | 0：正常 1：三级故障 | 339 | DiscreteInputs | 1 | AB | 1 | 0 |  | pileLinkageFaultSurgeTripFault | {"en":"Pile linkage fault - surge trip fault"}
1128 | 三级SD卡异常 | bool |  | 0：系统正常 1：一级预警 | 340 | DiscreteInputs | 1 | AB | 1 | 0 |  | thirdLevelSdCardAbnormality | {"en":"Third level SD card abnormality"}
1129 | 电磁阀主阀控制 | bool |  | 0：未使能 1：使能 | 343 | DiscreteInputs | 1 | AB | 1 | 0 |  | electromagneticValveMainValveControl | {"en":"Electromagnetic valve main valve control"}
1130 | 堆隔离开关分合闸异常 | bool |  | 0：正常 1：三级故障 | 344 | DiscreteInputs | 1 | AB | 1 | 0 |  | abnormalOpeningAndClosingOfTheStackIsolationSwitch | {"en":"Abnormal opening and closing of the stack isolation switch"}
1131 | 软件急停 | bool |  | 0：正常 1：三级故障 | 345 | DiscreteInputs | 1 | AB | 1 | 0 |  | softwareEmergencyStop | {"en":"Software emergency stop"}
1132 | EMU校时反馈 | bool |  |  | 346 | DiscreteInputs | 1 | AB | 1 | 0 |  | emuTimingFeedback | {"en":"EMU timing feedback"}
1133 | EMS校时反馈 | bool |  |  | 347 | DiscreteInputs | 1 | AB | 1 | 0 |  | emsTimingFeedback | {"en":"EMS timing feedback"}
1134 | 浪涌脱扣故障 | bool |  | 0：正常 1：三级故障 | 348 | DiscreteInputs | 1 | AB | 1 | 0 |  | surgeTrippingFault | {"en":"Surge tripping fault"}
1135 | 接触器控制异常 | bool |  | 0：正常 1：三级故障 | 350 | DiscreteInputs | 1 | AB | 1 | 0 |  | abnormalContactorControl | {"en":"Abnormal contactor control"}
1136 | 簇间电流失衡一级故障 | bool |  | 0：正常 1：三级故障 | 353 | DiscreteInputs | 1 | AB | 1 | 0 |  | firstLevelFaultOfCurrentImbalanceBetweenClusters | {"en":"First level fault of current imbalance between clusters"}
1137 | 簇间电流失衡二级告警 | bool |  | 0：系统正常 1：二级告警 | 354 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForCurrentImbalanceBetweenClusters | {"en":"Secondary alarm for current imbalance between clusters"}
1138 | 簇间电流失衡三级预警 | bool |  | 0：系统正常 1：三级预警 | 355 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForCurrentImbalanceBetweenClusters | {"en":"Three level warning for current imbalance between clusters"}
1139 | 堆间通讯故障 | bool |  | 0：正常 1：三级故障 | 358 | DiscreteInputs | 1 | AB | 1 | 0 |  | interStackCommunicationFailure | {"en":"Inter stack communication failure"}
1500 | 簇 1 簇启用/停用状态 | bool |  | 0：停用 1：启用 | 2001 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ClusterEnabledDisabledStatus | {"en":"Cluster 1 cluster enabled/disabled status"}
1501 | 簇 1 簇充电状态 | bool |  | 0：空闲 1：充电 | 2002 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingStatus | {"en":"Cluster 1 charging status"}
1502 | 簇 1 簇放电状态 | bool |  | 0：空闲 1：放电 | 2003 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeState | {"en":"Cluster 1 discharge state"}
1503 | 簇 1 簇一级故障 | bool |  | 0：系统正常 1：三级故障 | 2004 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1PrimaryFault | {"en":"Cluster 1 primary fault"}
1504 | 簇 1 簇二级告警 | bool |  | 0：系统正常 1：二级告警 | 2005 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ClusterLevel2Alarm | {"en":"Cluster 1 Cluster Level 2 Alarm"}
1505 | 簇 1 簇三级预警 | bool |  | 0：系统正常 1：一级预警 | 2006 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ClusterLevel3Warning | {"en":"Cluster 1 Cluster Level 3 Warning"}
1506 | 簇 1 簇禁充标志 | bool |  | 0：允许 1：禁止充电 | 2007 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ClusterNoChargingFlag | {"en":"Cluster 1 cluster no charging flag"}
1507 | 簇 1 簇禁放标志 | bool |  | 0：允许 1：禁止放电 | 2008 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ForbiddenFlag | {"en":"Cluster 1: Forbidden Flag"}
1508 | 簇 1 总正接触器状态 | bool |  | 0：断开 1：闭合 | 2009 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1TotalPositiveContactorStatus | {"en":"Cluster 1 total positive contactor status"}
1509 | 簇 1 总负接触器状态 | bool |  | 0：断开 1：闭合 | 2010 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1TotalNegativeContactorStatus | {"en":"Cluster 1 total negative contactor status"}
1510 | 簇 1 预充接触器状态 | bool |  | 0：断开 1：闭合 | 2011 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1PreChargingContactorStatus | {"en":"Cluster 1 Pre charging Contactor Status"}
1511 | 簇 1 运行灯接触器状态 | bool |  | 0：断开 1：闭合 | 2013 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1RunningLightContactorStatus | {"en":"Cluster 1 running light contactor status"}
1512 | 簇 1 故障灯接触器状态 | bool |  | 0：断开 1：闭合 | 2014 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1FaultLightContactorStatus | {"en":"Cluster 1 fault light contactor status"}
1513 | 簇 1 高压箱断路器/隔离开关状态 | bool |  | 0：断开 1：闭合 | 2015 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1HighVoltageBoxCircuitBreakerIsolationSwitchStatus | {"en":"Cluster 1 High Voltage Box Circuit Breaker/Isolation Switch Status"}
1514 | 簇 1 接触器总状态 | bool |  | 0：断开 1：闭合 | 2016 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ContactorOverallStatus | {"en":"Cluster 1 contactor overall status"}
1515 | 簇 1 总正接触器粘连 | bool |  | 0：正常 1：三级故障 | 2017 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1TotalPositiveContactorAdhesion | {"en":"Cluster 1 total positive contactor adhesion"}
1516 | 簇 1 总负接触器粘连 | bool |  | 0：正常 1：三级故障 | 2018 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1TotalNegativeContactorAdhesion | {"en":"Cluster 1 total negative contactor adhesion"}
1517 | 簇 1 总正接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2020 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1PositiveContactorStuck | {"en":"Cluster 1 positive contactor stuck"}
1518 | 簇 1 总负接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2021 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1TotalNegativeContactorStuck | {"en":"Cluster 1 total negative contactor stuck"}
1519 | 簇 1 单体电压采集故障 | bool |  | 0：正常 1：三级故障 | 2026 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1SingleCellVoltageAcquisitionFault | {"en":"Cluster 1 single cell voltage acquisition fault"}
1520 | 簇 1 单体温度采集故障 | bool |  | 0：正常 1：三级故障 | 2027 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1MonomerTemperatureAcquisitionFault | {"en":"Cluster 1 monomer temperature acquisition fault"}
1521 | 簇 1 INCAN接收异常 | bool |  | 0：正常 1：三级故障 | 2029 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1IncanReceivingException | {"en":"Cluster 1 INCAN receiving exception"}
1522 | 簇 1 BMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2030 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1BmuCommunicationFailure | {"en":"Cluster 1 BMU communication failure"}
1523 | 簇 1 BAMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2031 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1BamuCommunicationFailure | {"en":"Cluster 1 BAMU communication failure"}
1524 | 簇 1 充电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2033 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitOvervoltageLevel1Fault | {"en":"Cluster 1 charging unit overvoltage level 1 fault"}
1525 | 簇 1 放电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2034 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellOvervoltageLevel1Fault | {"en":"Cluster 1 discharge cell overvoltage level 1 fault"}
1526 | 簇 1 充电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2035 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitUndervoltageLevelOneFault | {"en":"Cluster 1 charging unit undervoltage level one fault"}
1527 | 簇 1 放电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2036 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellUndervoltagePrimaryFault | {"en":"Cluster 1 discharge cell undervoltage primary fault"}
1528 | 簇 1 充电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2037 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 1 charging unit voltage difference is too large, first level fault"}
1529 | 簇 1 放电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2038 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 1 discharge cell voltage difference is too large, first level fault"}
1530 | 簇 1 充电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2039 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingClusterTotalVoltageHighLevelOneFault | {"en":"Cluster 1 Charging Cluster Total Voltage High Level One Fault"}
1531 | 簇 1 放电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2040 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeClusterTotalVoltageTooHighLevelOneFault | {"en":"Cluster 1 discharge cluster total voltage too high level one fault"}
1532 | 簇 1 充电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2041 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 1 Charging Cluster Total Voltage Too Low Level One Fault"}
1533 | 簇 1 放电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2042 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 1 discharge cluster total voltage too low level one fault"}
1534 | 簇 1 充电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2043 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitHighTemperatureFirstLevelFault | {"en":"Cluster 1 charging unit high temperature first level fault"}
1535 | 簇 1 放电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2044 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellHighTemperaturePrimaryFault | {"en":"Cluster 1 discharge cell high temperature primary fault"}
1536 | 簇 1 充电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2045 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitLowTemperatureLevelOneFault | {"en":"Cluster 1 charging unit low temperature level one fault"}
1537 | 簇 1 放电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2046 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellLowTemperaturePrimaryFault | {"en":"Cluster 1 discharge cell low-temperature primary fault"}
1538 | 簇 1 充电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2047 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 1 charging unit temperature difference is too large, level 1 fault"}
1539 | 簇 1 放电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2048 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 1 discharge unit temperature difference is too large, level 1 fault"}
1540 | 簇 1 充电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2049 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingPackageRoomTotalVoltageDifferenceTooLargeLevelOneFault | {"en":"Cluster 1 Charging Package Room Total Voltage Difference Too Large Level One Fault"}
1541 | 簇 1 放电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2050 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargePacketTotalPressureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 1 discharge packet total pressure difference is too large, level 1 fault"}
1542 | 簇 1 充电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2051 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingPackTotalVoltageHighLevelOneFault | {"en":"Cluster 1 Charging Pack Total Voltage High Level One Fault"}
1543 | 簇 1 放电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2052 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargePacketTotalVoltageTooHighLevelOneFault | {"en":"Cluster 1 discharge packet total voltage too high level one fault"}
1544 | 簇 1 充电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2053 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingPackTotalVoltageTooLowLevelOneFault | {"en":"Cluster 1 Charging Pack Total Voltage Too Low Level One Fault"}
1545 | 簇 1 放电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2054 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargePacketTotalVoltageTooLowLevelOneFault | {"en":"Cluster 1 discharge packet total voltage too low level one fault"}
1546 | 簇 1 充电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2055 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingCurrentTooHighLevelOneFault | {"en":"Cluster 1 charging current too high level one fault"}
1547 | 簇 1 放电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2056 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCurrentTooHighLevelOneFault | {"en":"Cluster 1 discharge current too high level one fault"}
1548 | 簇 1 绝缘过低一级故障 | bool |  | 0：正常 1：三级故障 | 2057 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1InsulationLowLevelOneFault | {"en":"Cluster 1 insulation low level one fault"}
1549 | 簇 1 SOC过低一级故障 | bool |  | 0：正常 1：三级故障 | 2059 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1SocLowLevelOneFault | {"en":"Cluster 1 SOC low level one fault"}
1550 | 簇 1 热失控故障 | bool |  | 0：正常 1：三级故障 | 2060 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ThermalRunawayFault | {"en":"Cluster 1 thermal runaway fault"}
1551 | 簇 1 电流采集故障 | bool |  | 0：正常 1：三级故障 | 2061 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1CurrentAcquisitionFault | {"en":"Cluster 1 current acquisition fault"}
1552 | 簇 1 簇内压差过大故障 | bool |  | 0：正常 1：三级故障 | 2062 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1HasAFaultOfExcessivePressureDifferenceWithinTheCluster | {"en":"Cluster 1 has a fault of excessive pressure difference within the cluster"}
1553 | 簇 1 簇间压差过大故障 | bool |  | 0：正常 1：三级故障 | 2063 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1FaultOfExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 1: Fault of excessive pressure difference between clusters"}
1554 | 簇 1 管路漏液故障 | bool |  | 0：正常 1：三级故障 | 2064 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1PipelineLeakageFault | {"en":"Cluster 1 pipeline leakage fault"}
1555 | 簇 1 极柱温度采集故障 | bool |  | 0：正常 1：三级故障 | 2065 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1PoleTemperatureAcquisitionFault | {"en":"Cluster 1 pole temperature acquisition fault"}
1556 | 簇 1 充电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2069 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitOvervoltageLevel2Alarm | {"en":"Cluster 1 charging unit overvoltage level 2 alarm"}
1557 | 簇 1 放电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2070 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellOvervoltageLevel2Alarm | {"en":"Cluster 1 discharge cell overvoltage level 2 alarm"}
1558 | 簇 1 充电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2071 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitUndervoltageLevel2Alarm | {"en":"Cluster 1 charging unit undervoltage level 2 alarm"}
1559 | 簇 1 放电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2072 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellUndervoltageLevel2Alarm | {"en":"Cluster 1 discharge cell undervoltage level 2 alarm"}
1560 | 簇 1 充电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2073 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitVoltageDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 1 charging unit voltage difference is too large, level 2 alarm"}
1561 | 簇 1 放电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2074 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellPressureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 1 discharge cell pressure difference is too large, level 2 alarm"}
1562 | 簇 1 充电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2075 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingClusterTotalVoltageOverLevel2Alarm | {"en":"Cluster 1 Charging Cluster Total Voltage Over Level 2 Alarm"}
1563 | 簇 1 放电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2076 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeClusterTotalVoltageExceedsLevel2Alarm | {"en":"Cluster 1 discharge cluster total voltage exceeds level 2 alarm"}
1564 | 簇 1 充电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2077 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingClusterTotalVoltageLowLevel2Alarm | {"en":"Cluster 1 Charging Cluster Total Voltage Low Level 2 Alarm"}
1565 | 簇 1 放电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2078 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeClusterTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 1 discharge cluster total voltage too low level 2 alarm"}
1566 | 簇 1 充电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2079 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitHighTemperatureLevel2Alarm | {"en":"Cluster 1 charging unit high temperature level 2 alarm"}
1567 | 簇 1 放电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2080 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellHighTemperatureSecondaryAlarm | {"en":"Cluster 1 discharge cell high temperature secondary alarm"}
1568 | 簇 1 充电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2081 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitLowTemperatureLevel2Alarm | {"en":"Cluster 1 charging unit low temperature level 2 alarm"}
1569 | 簇 1 放电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2082 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellLowTemperatureSecondaryAlarm | {"en":"Cluster 1 discharge cell low temperature secondary alarm"}
1570 | 簇 1 充电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2083 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitTemperatureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 1 charging unit temperature difference is too large, level 2 alarm"}
1571 | 簇 1 放电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2084 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeUnitTemperatureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 1 discharge unit temperature difference is too large, level 2 alarm"}
1572 | 簇 1 充电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2085 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingPackageRoomTotalVoltageDifferenceTooHighLevel2Alarm | {"en":"Cluster 1 Charging Package Room Total Voltage Difference Too High Level 2 Alarm"}
1573 | 簇 1 放电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2086 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1SecondaryAlarmForExcessiveTotalPressureDifferenceBetweenDischargePackets | {"en":"Cluster 1: Secondary alarm for excessive total pressure difference between discharge packets"}
1574 | 簇 1 充电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2087 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingPackTotalVoltageOverLevel2Alarm | {"en":"Cluster 1 Charging Pack Total Voltage Over Level 2 Alarm"}
1575 | 簇 1 放电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2088 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargePacketTotalVoltageTooHighLevel2Alarm | {"en":"Cluster 1 discharge packet total voltage too high level 2 alarm"}
1576 | 簇 1 充电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2089 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingPackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 1 Charging Pack Total Voltage Too Low Level 2 Alarm"}
1577 | 簇 1 放电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2090 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargePacketTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 1 discharge packet total voltage too low level 2 alarm"}
1578 | 簇 1 充电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2091 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingCurrentTooHighLevel2Alarm | {"en":"Cluster 1 charging current too high level 2 alarm"}
1579 | 簇 1 放电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2092 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCurrentTooHighLevel2Alarm | {"en":"Cluster 1 discharge current too high level 2 alarm"}
1580 | 簇 1 绝缘过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2093 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1InsulationLowLevel2Alarm | {"en":"Cluster 1 insulation low level 2 alarm"}
1581 | 簇 1 SOC过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2095 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1SocLowLevel2Alarm | {"en":"Cluster 1 SOC Low Level 2 Alarm"}
1582 | 簇 1 充电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2096 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitOvervoltageLevel3Warning | {"en":"Cluster 1 Charging Unit Overvoltage Level 3 Warning"}
1583 | 簇 1 放电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2097 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellOvervoltageLevelThreeWarning | {"en":"Cluster 1 discharge cell overvoltage level three warning"}
1584 | 簇 1 充电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2098 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitUndervoltageLevel3Warning | {"en":"Cluster 1 Charging Unit Undervoltage Level 3 Warning"}
1585 | 簇 1 放电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2099 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellUndervoltageThreeLevelWarning | {"en":"Cluster 1 discharge cell undervoltage three-level warning"}
1586 | 簇 1 充电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2100 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1Level3WarningForExcessiveVoltageDifferenceInChargingCells | {"en":"Cluster 1: Level 3 warning for excessive voltage difference in charging cells"}
1587 | 簇 1 放电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2101 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ThreeLevelWarningForExcessiveDischargeCellPressureDifference | {"en":"Cluster 1: Three level warning for excessive discharge cell pressure difference"}
1588 | 簇 1 充电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2102 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingClusterTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 1 Charging Cluster Total Voltage Over High Level Three Warning"}
1589 | 簇 1 放电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2103 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeClusterTotalPressureHighThreeLevelWarning | {"en":"Cluster 1 discharge cluster total pressure high three level warning"}
1590 | 簇 1 充电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2104 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingClusterTotalVoltageLowLevelThreeWarning | {"en":"Cluster 1 Charging Cluster Total Voltage Low Level Three Warning"}
1591 | 簇 1 放电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2105 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeClusterTotalPressureTooLowThreeLevelWarning | {"en":"Cluster 1 discharge cluster total pressure too low three-level warning"}
1592 | 簇 1 充电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2106 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 1 Charging Unit High Temperature Level Three Warning"}
1593 | 簇 1 放电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2107 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellHighTemperatureLevelThreeWarning | {"en":"Cluster 1 discharge cell high temperature level three warning"}
1594 | 簇 1 充电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2108 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitLowTemperatureLevelThreeWarning | {"en":"Cluster 1 Charging Unit Low Temperature Level Three Warning"}
1595 | 簇 1 放电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2109 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeCellLowTemperatureThreeLevelWarning | {"en":"Cluster 1 discharge cell low temperature three-level warning"}
1596 | 簇 1 充电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2110 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingUnitLevel3WarningForExcessiveTemperatureDifference | {"en":"Cluster 1 Charging Unit: Level 3 Warning for Excessive Temperature Difference"}
1597 | 簇 1 放电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2111 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargeUnitTemperatureDifferenceIsTooLargeLevel3Warning | {"en":"Cluster 1 discharge unit temperature difference is too large, level 3 warning"}
1598 | 簇 1 充电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2112 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ThreeLevelWarningForExcessiveTotalVoltageDifferenceBetweenChargingBags | {"en":"Cluster 1: Three level warning for excessive total voltage difference between charging bags"}
1599 | 簇 1 放电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2113 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ThreeLevelWarningForExcessiveTotalPressureDifferenceBetweenDischargePackets | {"en":"Cluster 1: Three level warning for excessive total pressure difference between discharge packets"}
1600 | 簇 1 充电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2114 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingPackTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 1 Charging Pack Total Voltage Over High Level Three Warning"}
1601 | 簇 1 放电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2115 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargePackageTotalPressureHighThreeLevelWarning | {"en":"Cluster 1 discharge package total pressure high three level warning"}
1602 | 簇 1 充电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2116 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ChargingPackTotalVoltageLowLevelThreeWarning | {"en":"Cluster 1 Charging Pack Total Voltage Low Level Three Warning"}
1603 | 簇 1 放电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2117 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1DischargePackageTotalPressureTooLowLevel3Warning | {"en":"Cluster 1 discharge package total pressure too low Level 3 warning"}
1604 | 簇 1 充电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2118 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1Level3WarningForExcessiveChargingCurrent | {"en":"Cluster 1: Level 3 warning for excessive charging current"}
1605 | 簇 1 放电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2119 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ThreeLevelWarningForExcessiveDischargeCurrent | {"en":"Cluster 1: Three level warning for excessive discharge current"}
1606 | 簇 1 绝缘过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2120 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1InsulationLowLevelThreeWarning | {"en":"Cluster 1 insulation low level three warning"}
1607 | 簇 1 SOC过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2122 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1SocLowLevelThreeWarning | {"en":"Cluster 1 SOC Low Level Three Warning"}
1608 | 簇 1 温升告警 | bool |  | 0：系统正常 1：一级预警 | 2123 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1TemperatureRiseAlarm | {"en":"Cluster 1 temperature rise alarm"}
1609 | 簇 1 BCMU序列号异常预警 | bool |  | 0：系统正常 1：一级预警 | 2124 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1BcmuSerialNumberAbnormalWarning | {"en":"Cluster 1 BCMU serial number abnormal warning"}
1610 | 簇 1 簇间压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2125 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1ThreeLevelWarningForExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 1: Three level warning for excessive pressure difference between clusters"}
1611 | 簇 1 二级SD卡异常 | bool |  | 0：系统正常 1：一级预警 | 2126 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1Level2SdCardException | {"en":"Cluster 1 Level 2 SD Card Exception"}
1612 | 簇 1 电磁阀控制模块通讯异常 | bool |  | 0：正常 1：电磁阀模块通讯异常（一级预警） | 2127 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1SolenoidValveControlModuleCommunicationAbnormality | {"en":"Cluster 1 solenoid valve control module communication abnormality"}
1613 | 簇 1 系统故障下电 | bool |  | 0：正常 1：下发故障（三级故障） | 2128 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1SystemFailurePowerOff | {"en":"Cluster 1 system failure power off"}
1614 | 簇 1 BCMU校时反馈 | bool |  | 0：正常 1：已较时 | 2129 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster1BcmuTimingFeedback | {"en":"Cluster 1 BCMU timing feedback"}
1615 | 簇 2 簇启用/停用状态 | bool |  | 0：停用 1：启用 | 2130 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ClusterEnabledDisabledStatus | {"en":"Cluster 2 cluster enabled/disabled status"}
1616 | 簇 2 簇充电状态 | bool |  | 0：空闲 1：充电 | 2131 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingStatus | {"en":"Cluster 2 charging status"}
1617 | 簇 2 簇放电状态 | bool |  | 0：空闲 1：放电 | 2132 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeState | {"en":"Cluster 2 discharge state"}
1618 | 簇 2 簇一级故障 | bool |  | 0：系统正常 1：三级故障 | 2133 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ClusterFirstLevelFault | {"en":"Cluster 2 cluster first level fault"}
1619 | 簇 2 簇二级告警 | bool |  | 0：系统正常 1：二级告警 | 2134 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ClusterLevel2Alarm | {"en":"Cluster 2 Cluster Level 2 Alarm"}
1620 | 簇 2 簇三级预警 | bool |  | 0：系统正常 1：一级预警 | 2135 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ClusterLevel3Warning | {"en":"Cluster 2 Cluster Level 3 Warning"}
1621 | 簇 2 簇禁充标志 | bool |  | 0：允许 1：禁止充电 | 2136 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ForbiddenChargingFlag | {"en":"Cluster 2: Forbidden Charging Flag"}
1622 | 簇 2 簇禁放标志 | bool |  | 0：允许 1：禁止放电 | 2137 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ForbiddenFlag | {"en":"Cluster 2: Forbidden Flag"}
1623 | 簇 2 总正接触器状态 | bool |  | 0：断开 1：闭合 | 2138 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2TotalPositiveContactorStatus | {"en":"Cluster 2 total positive contactor status"}
1624 | 簇 2 总负接触器状态 | bool |  | 0：断开 1：闭合 | 2139 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2TotalNegativeContactorStatus | {"en":"Cluster 2 total negative contactor status"}
1625 | 簇 2 预充接触器状态 | bool |  | 0：断开 1：闭合 | 2140 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2PreChargingContactorStatus | {"en":"Cluster 2 Pre charging Contactor Status"}
1626 | 簇 2 运行灯接触器状态 | bool |  | 0：断开 1：闭合 | 2142 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2RunningLightContactorStatus | {"en":"Cluster 2 running light contactor status"}
1627 | 簇 2 故障灯接触器状态 | bool |  | 0：断开 1：闭合 | 2143 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2FaultLightContactorStatus | {"en":"Cluster 2 fault light contactor status"}
1628 | 簇 2 高压箱断路器/隔离开关状态 | bool |  | 0：断开 1：闭合 | 2144 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2HighVoltageBoxCircuitBreakerIsolationSwitchStatus | {"en":"Cluster 2 High Voltage Box Circuit Breaker/Isolation Switch Status"}
1629 | 簇 2 接触器总状态 | bool |  | 0：断开 1：闭合 | 2145 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ContactorOverallStatus | {"en":"Cluster 2 contactor overall status"}
1630 | 簇 2 总正接触器粘连 | bool |  | 0：正常 1：三级故障 | 2146 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2TotalPositiveContactorAdhesion | {"en":"Cluster 2 total positive contactor adhesion"}
1631 | 簇 2 总负接触器粘连 | bool |  | 0：正常 1：三级故障 | 2147 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2TotalNegativeContactorAdhesion | {"en":"Cluster 2 total negative contactor adhesion"}
1632 | 簇 2 总正接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2149 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2TotalPositiveContactorStuck | {"en":"Cluster 2 total positive contactor stuck"}
1633 | 簇 2 总负接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2150 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2TotalNegativeContactorStuck | {"en":"Cluster 2 total negative contactor stuck"}
1634 | 簇 2 单体电压采集故障 | bool |  | 0：正常 1：三级故障 | 2155 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2SingleCellVoltageAcquisitionFault | {"en":"Cluster 2 single cell voltage acquisition fault"}
1635 | 簇 2 单体温度采集故障 | bool |  | 0：正常 1：三级故障 | 2156 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2MonomerTemperatureAcquisitionFault | {"en":"Cluster 2 monomer temperature acquisition fault"}
1636 | 簇 2 INCAN接收异常 | bool |  | 0：正常 1：三级故障 | 2158 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2IncanReceivingException | {"en":"Cluster 2 INCAN receiving exception"}
1637 | 簇 2 BMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2159 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2BmuCommunicationFailure | {"en":"Cluster 2 BMU communication failure"}
1638 | 簇 2 BAMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2160 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2BamuCommunicationFailure | {"en":"Cluster 2 BAMU communication failure"}
1639 | 簇 2 充电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2162 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitOvervoltageLevel1Fault | {"en":"Cluster 2 charging unit overvoltage level 1 fault"}
1640 | 簇 2 放电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2163 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellOvervoltageLevel1Fault | {"en":"Cluster 2 discharge cell overvoltage level 1 fault"}
1641 | 簇 2 充电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2164 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitUndervoltageLevel1Fault | {"en":"Cluster 2 charging unit undervoltage level 1 fault"}
1642 | 簇 2 放电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2165 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellUndervoltagePrimaryFault | {"en":"Cluster 2 discharge cell undervoltage primary fault"}
1643 | 簇 2 充电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2166 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitVoltageDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 2 charging unit voltage difference is too large, level 1 fault"}
1644 | 簇 2 放电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2167 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 2 discharge cell voltage difference is too large, first level fault"}
1645 | 簇 2 充电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2168 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingClusterTotalVoltageHighLevelOneFault | {"en":"Cluster 2 Charging Cluster Total Voltage High Level One Fault"}
1646 | 簇 2 放电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2169 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeClusterTotalVoltageTooHighLevelOneFault | {"en":"Cluster 2 discharge cluster total voltage too high level one fault"}
1647 | 簇 2 充电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2170 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 2 Charging Cluster Total Voltage Too Low Level One Fault"}
1648 | 簇 2 放电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2171 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 2 discharge cluster total voltage too low level one fault"}
1649 | 簇 2 充电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2172 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitHighTemperatureFirstLevelFault | {"en":"Cluster 2 charging unit high temperature first level fault"}
1650 | 簇 2 放电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2173 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeUnitHighTemperaturePrimaryFault | {"en":"Cluster 2 discharge unit high temperature primary fault"}
1651 | 簇 2 充电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2174 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitLowTemperaturePrimaryFault | {"en":"Cluster 2 charging unit low-temperature primary fault"}
1652 | 簇 2 放电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2175 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellLowTemperaturePrimaryFault | {"en":"Cluster 2 discharge cell low-temperature primary fault"}
1653 | 簇 2 充电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2176 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 2 charging unit temperature difference is too large, level 1 fault"}
1654 | 簇 2 放电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2177 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 2 discharge unit temperature difference is too large, level 1 fault"}
1655 | 簇 2 充电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2178 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingPackageRoomTotalVoltageDifferenceTooLargeLevelOneFault | {"en":"Cluster 2 Charging Package Room Total Voltage Difference Too Large Level One Fault"}
1656 | 簇 2 放电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2179 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargePacketTotalPressureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 2 discharge packet total pressure difference is too large, level 1 fault"}
1657 | 簇 2 充电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2180 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingPackTotalVoltageHighLevelOneFault | {"en":"Cluster 2 Charging Pack Total Voltage High Level One Fault"}
1658 | 簇 2 放电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2181 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargePacketTotalVoltageTooHighLevelOneFault | {"en":"Cluster 2 discharge packet total voltage too high level one fault"}
1659 | 簇 2 充电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2182 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingPackTotalVoltageTooLowLevelOneFault | {"en":"Cluster 2 Charging Pack Total Voltage Too Low Level One Fault"}
1660 | 簇 2 放电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2183 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargePacketTotalVoltageTooLowLevelOneFault | {"en":"Cluster 2 discharge packet total voltage too low level one fault"}
1661 | 簇 2 充电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2184 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingCurrentTooHighLevelOneFault | {"en":"Cluster 2 charging current too high level one fault"}
1662 | 簇 2 放电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2185 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCurrentTooHighLevelOneFault | {"en":"Cluster 2 discharge current too high level one fault"}
1663 | 簇 2 绝缘过低一级故障 | bool |  | 0：正常 1：三级故障 | 2186 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2InsulationLowLevelOneFault | {"en":"Cluster 2 insulation low level one fault"}
1664 | 簇 2 SOC过低一级故障 | bool |  | 0：正常 1：三级故障 | 2188 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2SocLowLevelOneFault | {"en":"Cluster 2 SOC low level one fault"}
1665 | 簇 2 热失控故障 | bool |  | 0：正常 1：三级故障 | 2189 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ThermalRunawayFault | {"en":"Cluster 2 thermal runaway fault"}
1666 | 簇 2 电流采集故障 | bool |  | 0：正常 1：三级故障 | 2190 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2CurrentAcquisitionFault | {"en":"Cluster 2 current acquisition fault"}
1667 | 簇 2 簇内压差过大故障 | bool |  | 0：正常 1：三级故障 | 2191 | DiscreteInputs | 1 | AB | 1 | 0 |  | faultOfExcessivePressureDifferenceWithinCluster2 | {"en":"Fault of excessive pressure difference within cluster 2"}
1668 | 簇 2 簇间压差过大故障 | bool |  | 0：正常 1：三级故障 | 2192 | DiscreteInputs | 1 | AB | 1 | 0 |  | faultOfExcessivePressureDifferenceBetweenClusters2 | {"en":"Fault of excessive pressure difference between clusters 2"}
1669 | 簇 2 管路漏液故障 | bool |  | 0：正常 1：三级故障 | 2193 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2PipelineLeakageFault | {"en":"Cluster 2 pipeline leakage fault"}
1670 | 簇 2 极柱温度采集故障 | bool |  | 0：正常 1：三级故障 | 2194 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2PoleTemperatureAcquisitionFault | {"en":"Cluster 2 pole temperature acquisition fault"}
1671 | 簇 2 充电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2198 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitOvervoltageLevel2Alarm | {"en":"Cluster 2 charging unit overvoltage level 2 alarm"}
1672 | 簇 2 放电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2199 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellOvervoltageLevel2Alarm | {"en":"Cluster 2 discharge cell overvoltage level 2 alarm"}
1673 | 簇 2 充电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2200 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitUndervoltageLevel2Alarm | {"en":"Cluster 2 charging unit undervoltage level 2 alarm"}
1674 | 簇 2 放电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2201 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellUndervoltageLevel2Alarm | {"en":"Cluster 2 discharge cell undervoltage level 2 alarm"}
1675 | 簇 2 充电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2202 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitVoltageDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 2 charging unit voltage difference is too large, level 2 alarm"}
1676 | 簇 2 放电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2203 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellPressureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 2 discharge cell pressure difference is too large, level 2 alarm"}
1677 | 簇 2 充电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2204 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingClusterTotalVoltageOverLevel2Alarm | {"en":"Cluster 2 Charging Cluster Total Voltage Over Level 2 Alarm"}
1678 | 簇 2 放电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2205 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeClusterTotalVoltageOverHighLevel2Alarm | {"en":"Cluster 2 discharge cluster total voltage over high level 2 alarm"}
1679 | 簇 2 充电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2206 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingClusterTotalVoltageLowLevel2Alarm | {"en":"Cluster 2 Charging Cluster Total Voltage Low Level 2 Alarm"}
1680 | 簇 2 放电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2207 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeClusterTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 2 discharge cluster total voltage too low level 2 alarm"}
1681 | 簇 2 充电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2208 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitHighTemperatureLevel2Alarm | {"en":"Cluster 2 charging unit high temperature level 2 alarm"}
1682 | 簇 2 放电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2209 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeUnitHighTemperatureSecondaryAlarm | {"en":"Cluster 2 discharge unit high temperature secondary alarm"}
1683 | 簇 2 充电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2210 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitLowTemperatureLevel2Alarm | {"en":"Cluster 2 charging unit low temperature level 2 alarm"}
1684 | 簇 2 放电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2211 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellLowTemperatureSecondaryAlarm | {"en":"Cluster 2 discharge cell low temperature secondary alarm"}
1685 | 簇 2 充电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2212 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitLevel2AlarmForExcessiveTemperatureDifference | {"en":"Cluster 2 Charging Unit: Level 2 Alarm for Excessive Temperature Difference"}
1686 | 簇 2 放电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2213 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeUnitTemperatureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 2 discharge unit temperature difference is too large, level 2 alarm"}
1687 | 簇 2 充电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2214 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingPackageRoomTotalVoltageDifferenceTooHighLevel2Alarm | {"en":"Cluster 2 Charging Package Room Total Voltage Difference Too High Level 2 Alarm"}
1688 | 簇 2 放电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2215 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondLevelAlarmForExcessiveTotalPressureDifferenceBetweenCluster2DischargePackets | {"en":"Second level alarm for excessive total pressure difference between cluster 2 discharge packets"}
1689 | 簇 2 充电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2216 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingPackTotalVoltageOverLevel2Alarm | {"en":"Cluster 2 Charging Pack Total Voltage Over Level 2 Alarm"}
1690 | 簇 2 放电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2217 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargePackTotalVoltageHighLevel2Alarm | {"en":"Cluster 2 discharge pack total voltage high level 2 alarm"}
1691 | 簇 2 充电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2218 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingPackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 2 Charging Pack Total Voltage Too Low Level 2 Alarm"}
1692 | 簇 2 放电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2219 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargePackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 2 discharge pack total voltage too low level 2 alarm"}
1693 | 簇 2 充电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2220 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2Level2AlarmForExcessiveChargingCurrent | {"en":"Cluster 2: Level 2 alarm for excessive charging current"}
1694 | 簇 2 放电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2221 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCurrentTooHighLevel2Alarm | {"en":"Cluster 2 discharge current too high level 2 alarm"}
1695 | 簇 2 绝缘过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2222 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2InsulationLowLevel2Alarm | {"en":"Cluster 2 insulation low level 2 alarm"}
1696 | 簇 2 SOC过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2224 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2SocLowLevel2Alarm | {"en":"Cluster 2 SOC Low Level 2 Alarm"}
1697 | 簇 2 充电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2225 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitOvervoltageLevel3Warning | {"en":"Cluster 2 Charging Unit Overvoltage Level 3 Warning"}
1698 | 簇 2 放电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2226 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellOvervoltageLevelThreeWarning | {"en":"Cluster 2 discharge cell overvoltage level three warning"}
1699 | 簇 2 充电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2227 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitUndervoltageLevel3Warning | {"en":"Cluster 2 Charging Unit Undervoltage Level 3 Warning"}
1700 | 簇 2 放电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2228 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellUndervoltageThreeLevelWarning | {"en":"Cluster 2 discharge cell undervoltage three-level warning"}
1701 | 簇 2 充电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2229 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitVoltageDifferenceExcessiveLevel3Warning | {"en":"Cluster 2 Charging Unit Voltage Difference Excessive Level 3 Warning"}
1702 | 簇 2 放电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2230 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ThreeLevelWarningForExcessiveDischargeCellPressureDifference | {"en":"Cluster 2: Three level warning for excessive discharge cell pressure difference"}
1703 | 簇 2 充电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2231 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingClusterTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 2 Charging Cluster Total Voltage Over High Level Three Warning"}
1704 | 簇 2 放电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2232 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeClusterTotalPressureHighThreeLevelWarning | {"en":"Cluster 2 discharge cluster total pressure high three level warning"}
1705 | 簇 2 充电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2233 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingClusterTotalVoltageLowLevelThreeWarning | {"en":"Cluster 2 Charging Cluster Total Voltage Low Level Three Warning"}
1706 | 簇 2 放电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2234 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeClusterTotalVoltageTooLowThreeLevelWarning | {"en":"Cluster 2 discharge cluster total voltage too low three-level warning"}
1707 | 簇 2 充电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2235 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitHighTemperatureLevel3Warning | {"en":"Cluster 2 Charging Unit High Temperature Level 3 Warning"}
1708 | 簇 2 放电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2236 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 2 discharge unit high temperature level three warning"}
1709 | 簇 2 充电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2237 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitLowTemperatureLevelThreeWarning | {"en":"Cluster 2 Charging Unit Low Temperature Level Three Warning"}
1710 | 簇 2 放电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2238 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeCellLowTemperatureThreeLevelWarning | {"en":"Cluster 2 discharge cell low temperature three-level warning"}
1711 | 簇 2 充电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2239 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingUnitLevel3WarningForExcessiveTemperatureDifference | {"en":"Cluster 2 Charging Unit: Level 3 Warning for Excessive Temperature Difference"}
1712 | 簇 2 放电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2240 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargeUnitTemperatureDifferenceIsTooLargeLevel3Warning | {"en":"Cluster 2 discharge unit temperature difference is too large, level 3 warning"}
1713 | 簇 2 充电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2241 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ThreeLevelWarningForExcessiveTotalVoltageDifferenceBetweenChargingBags | {"en":"Cluster 2: Three level warning for excessive total voltage difference between charging bags"}
1714 | 簇 2 放电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2242 | DiscreteInputs | 1 | AB | 1 | 0 |  | threeLevelWarningForExcessiveTotalPressureDifferenceBetweenCluster2DischargePackets | {"en":"Three level warning for excessive total pressure difference between cluster 2 discharge packets"}
1715 | 簇 2 充电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2243 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingPackTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 2 Charging Pack Total Voltage Over High Level Three Warning"}
1716 | 簇 2 放电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2244 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargePackageTotalPressureHighThreeLevelWarning | {"en":"Cluster 2 discharge package total pressure high three level warning"}
1717 | 簇 2 充电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2245 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ChargingPackTotalVoltageLowLevelThreeWarning | {"en":"Cluster 2 Charging Pack Total Voltage Low Level Three Warning"}
1718 | 簇 2 放电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2246 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2DischargePackageTotalPressureTooLowLevel3Warning | {"en":"Cluster 2 discharge package total pressure too low Level 3 warning"}
1719 | 簇 2 充电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2247 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2Level3WarningForExcessiveChargingCurrent | {"en":"Cluster 2: Level 3 warning for excessive charging current"}
1720 | 簇 2 放电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2248 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ThreeLevelWarningForExcessiveDischargeCurrent | {"en":"Cluster 2: Three level warning for excessive discharge current"}
1721 | 簇 2 绝缘过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2249 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2InsulationLowLevelThreeWarning | {"en":"Cluster 2 insulation low level three warning"}
1722 | 簇 2 SOC过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2251 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2SocLowLevelThreeWarning | {"en":"Cluster 2 SOC Low Level Three Warning"}
1723 | 簇 2 温升告警 | bool |  | 0：系统正常 1：一级预警 | 2252 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2TemperatureRiseAlarm | {"en":"Cluster 2 temperature rise alarm"}
1724 | 簇 2 BCMU序列号异常预警 | bool |  | 0：系统正常 1：一级预警 | 2253 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2BcmuSerialNumberAnomalyWarning | {"en":"Cluster 2 BCMU serial number anomaly warning"}
1725 | 簇 2 簇间压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2254 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2ThreeLevelWarningForExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 2: Three level warning for excessive pressure difference between clusters"}
1726 | 簇 2 二级SD卡异常 | bool |  | 0：系统正常 1：一级预警 | 2255 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2Level2SdCardException | {"en":"Cluster 2 Level 2 SD Card Exception"}
1727 | 簇 2 电磁阀控制模块通讯异常 | bool |  | 0：正常 1：电磁阀模块通讯异常（一级预警） | 2256 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2SolenoidValveControlModuleCommunicationAbnormality | {"en":"Cluster 2 solenoid valve control module communication abnormality"}
1728 | 簇 2 系统故障下电 | bool |  | 0：正常 1：下发故障（三级故障） | 2257 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2SystemFailurePowerOff | {"en":"Cluster 2 system failure power off"}
1729 | 簇 2 BCMU校时反馈 | bool |  | 0：正常 1：已较时 | 2258 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster2BcmuTimingFeedback | {"en":"Cluster 2 BCMU timing feedback"}
1730 | 簇 3 簇启用/停用状态 | bool |  | 0：停用 1：启用 | 2259 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3EnableDisableStatus | {"en":"Cluster 3: Enable/Disable Status"}
1731 | 簇 3 簇充电状态 | bool |  | 0：空闲 1：充电 | 2260 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingStatus | {"en":"Cluster 3 charging status"}
1732 | 簇 3 簇放电状态 | bool |  | 0：空闲 1：放电 | 2261 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeState | {"en":"Cluster 3 discharge state"}
1733 | 簇 3 簇一级故障 | bool |  | 0：系统正常 1：三级故障 | 2262 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ClusterFirstLevelFault | {"en":"Cluster 3 cluster first level fault"}
1734 | 簇 3 簇二级告警 | bool |  | 0：系统正常 1：二级告警 | 2263 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ClusterLevel2Alarm | {"en":"Cluster 3 Cluster Level 2 Alarm"}
1735 | 簇 3 簇三级预警 | bool |  | 0：系统正常 1：一级预警 | 2264 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3Cluster3Level3Warning | {"en":"Cluster 3, Cluster 3, Level 3 Warning"}
1736 | 簇 3 簇禁充标志 | bool |  | 0：允许 1：禁止充电 | 2265 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ForbiddenChargingFlag | {"en":"Cluster 3: Forbidden Charging Flag"}
1737 | 簇 3 簇禁放标志 | bool |  | 0：允许 1：禁止放电 | 2266 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ForbiddenSigns | {"en":"Cluster 3: Forbidden Signs"}
1738 | 簇 3 总正接触器状态 | bool |  | 0：断开 1：闭合 | 2267 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3TotalPositiveContactorStatus | {"en":"Cluster 3 total positive contactor status"}
1739 | 簇 3 总负接触器状态 | bool |  | 0：断开 1：闭合 | 2268 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3TotalNegativeContactorStatus | {"en":"Cluster 3 total negative contactor status"}
1740 | 簇 3 预充接触器状态 | bool |  | 0：断开 1：闭合 | 2269 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3PreChargingContactorStatus | {"en":"Cluster 3 Pre charging Contactor Status"}
1741 | 簇 3 运行灯接触器状态 | bool |  | 0：断开 1：闭合 | 2271 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3RunningLightContactorStatus | {"en":"Cluster 3 running light contactor status"}
1742 | 簇 3 故障灯接触器状态 | bool |  | 0：断开 1：闭合 | 2272 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3FaultLightContactorStatus | {"en":"Cluster 3 fault light contactor status"}
1743 | 簇 3 高压箱断路器/隔离开关状态 | bool |  | 0：断开 1：闭合 | 2273 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3HighVoltageBoxCircuitBreakerIsolationSwitchStatus | {"en":"Cluster 3 High Voltage Box Circuit Breaker/Isolation Switch Status"}
1744 | 簇 3 接触器总状态 | bool |  | 0：断开 1：闭合 | 2274 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ContactorOverallStatus | {"en":"Cluster 3 contactor overall status"}
1745 | 簇 3 总正接触器粘连 | bool |  | 0：正常 1：三级故障 | 2275 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3TotalPositiveContactorAdhesion | {"en":"Cluster 3 total positive contactor adhesion"}
1746 | 簇 3 总负接触器粘连 | bool |  | 0：正常 1：三级故障 | 2276 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3TotalNegativeContactorAdhesion | {"en":"Cluster 3 total negative contactor adhesion"}
1747 | 簇 3 总正接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2278 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3TotalPositiveContactorStuck | {"en":"Cluster 3 total positive contactor stuck"}
1748 | 簇 3 总负接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2279 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3TotalNegativeContactorStuck | {"en":"Cluster 3 total negative contactor stuck"}
1749 | 簇 3 单体电压采集故障 | bool |  | 0：正常 1：三级故障 | 2284 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3SingleCellVoltageAcquisitionFault | {"en":"Cluster 3 single cell voltage acquisition fault"}
1750 | 簇 3 单体温度采集故障 | bool |  | 0：正常 1：三级故障 | 2285 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3MonomerTemperatureAcquisitionFault | {"en":"Cluster 3 monomer temperature acquisition fault"}
1751 | 簇 3 INCAN接收异常 | bool |  | 0：正常 1：三级故障 | 2287 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3IncanReceivingException | {"en":"Cluster 3 INCAN receiving exception"}
1752 | 簇 3 BMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2288 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3BmuCommunicationFailure | {"en":"Cluster 3 BMU communication failure"}
1753 | 簇 3 BAMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2289 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3BamuCommunicationFailure | {"en":"Cluster 3 BAMU communication failure"}
1754 | 簇 3 充电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2291 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitOvervoltageLevel1Fault | {"en":"Cluster 3 charging unit overvoltage level 1 fault"}
1755 | 簇 3 放电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2292 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellOvervoltageLevel1Fault | {"en":"Cluster 3 discharge cell overvoltage level 1 fault"}
1756 | 簇 3 充电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2293 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitUndervoltageLevel1Fault | {"en":"Cluster 3 charging unit undervoltage level 1 fault"}
1757 | 簇 3 放电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2294 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellUndervoltagePrimaryFault | {"en":"Cluster 3 discharge cell undervoltage primary fault"}
1758 | 簇 3 充电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2295 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitVoltageDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 3 charging unit voltage difference is too large, level 1 fault"}
1759 | 簇 3 放电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2296 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 3 discharge cell voltage difference is too large, first level fault"}
1760 | 簇 3 充电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2297 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingClusterTotalVoltageHighLevelOneFault | {"en":"Cluster 3 Charging Cluster Total Voltage High Level One Fault"}
1761 | 簇 3 放电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2298 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeClusterTotalVoltageTooHighLevelOneFault | {"en":"Cluster 3 discharge cluster total voltage too high level one fault"}
1762 | 簇 3 充电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2299 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 3 Charging Cluster Total Voltage Too Low Level One Fault"}
1763 | 簇 3 放电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2300 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 3 discharge cluster total voltage too low level one fault"}
1764 | 簇 3 充电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2301 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitHighTemperatureFirstLevelFault | {"en":"Cluster 3 charging unit high temperature first level fault"}
1765 | 簇 3 放电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2302 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeUnitHighTemperaturePrimaryFault | {"en":"Cluster 3 discharge unit high temperature primary fault"}
1766 | 簇 3 充电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2303 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitLowTemperatureLevelOneFault | {"en":"Cluster 3 charging unit low temperature level one fault"}
1767 | 簇 3 放电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2304 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellLowTemperaturePrimaryFault | {"en":"Cluster 3 discharge cell low-temperature primary fault"}
1768 | 簇 3 充电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2305 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 3 charging unit temperature difference is too large, level 1 fault"}
1769 | 簇 3 放电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2306 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 3 discharge unit temperature difference is too large, level 1 fault"}
1770 | 簇 3 充电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2307 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingPackageRoomTotalVoltageDifferenceTooLargeLevelOneFault | {"en":"Cluster 3 Charging Package Room Total Voltage Difference Too Large Level One Fault"}
1771 | 簇 3 放电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2308 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargePacketTotalPressureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 3 discharge packet total pressure difference is too large, level 1 fault"}
1772 | 簇 3 充电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2309 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingPackTotalVoltageHighLevelOneFault | {"en":"Cluster 3 Charging Pack Total Voltage High Level One Fault"}
1773 | 簇 3 放电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2310 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargePacketTotalVoltageTooHighLevelOneFault | {"en":"Cluster 3 discharge packet total voltage too high level one fault"}
1774 | 簇 3 充电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2311 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingPackTotalVoltageTooLowLevelOneFault | {"en":"Cluster 3 Charging Pack Total Voltage Too Low Level One Fault"}
1775 | 簇 3 放电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2312 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargePacketTotalVoltageTooLowLevelOneFault | {"en":"Cluster 3 discharge packet total voltage too low level one fault"}
1776 | 簇 3 充电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2313 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingCurrentTooHighLevelOneFault | {"en":"Cluster 3 charging current too high level one fault"}
1777 | 簇 3 放电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2314 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCurrentTooHighLevelOneFault | {"en":"Cluster 3 discharge current too high level one fault"}
1778 | 簇 3 绝缘过低一级故障 | bool |  | 0：正常 1：三级故障 | 2315 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3InsulationLowLevelOneFault | {"en":"Cluster 3 insulation low level one fault"}
1779 | 簇 3 SOC过低一级故障 | bool |  | 0：正常 1：三级故障 | 2317 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3SocLowLevelOneFault | {"en":"Cluster 3 SOC low level one fault"}
1780 | 簇 3 热失控故障 | bool |  | 0：正常 1：三级故障 | 2318 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ThermalRunawayFault | {"en":"Cluster 3 thermal runaway fault"}
1781 | 簇 3 电流采集故障 | bool |  | 0：正常 1：三级故障 | 2319 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3CurrentAcquisitionFault | {"en":"Cluster 3 current acquisition fault"}
1782 | 簇 3 簇内压差过大故障 | bool |  | 0：正常 1：三级故障 | 2320 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3FaultOfExcessivePressureDifferenceWithinCluster | {"en":"Cluster 3: Fault of excessive pressure difference within cluster"}
1783 | 簇 3 簇间压差过大故障 | bool |  | 0：正常 1：三级故障 | 2321 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3FaultOfExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 3: Fault of excessive pressure difference between clusters"}
1784 | 簇 3 管路漏液故障 | bool |  | 0：正常 1：三级故障 | 2322 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3PipelineLeakageFault | {"en":"Cluster 3 pipeline leakage fault"}
1785 | 簇 3 极柱温度采集故障 | bool |  | 0：正常 1：三级故障 | 2323 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3PoleTemperatureAcquisitionFault | {"en":"Cluster 3 pole temperature acquisition fault"}
1786 | 簇 3 充电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2327 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitOvervoltageLevel2Alarm | {"en":"Cluster 3 charging unit overvoltage level 2 alarm"}
1787 | 簇 3 放电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2328 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellOvervoltageLevel2Alarm | {"en":"Cluster 3 discharge cell overvoltage level 2 alarm"}
1788 | 簇 3 充电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2329 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitUndervoltageLevel2Alarm | {"en":"Cluster 3 charging unit undervoltage level 2 alarm"}
1789 | 簇 3 放电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2330 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellUndervoltageLevel2Alarm | {"en":"Cluster 3 discharge cell undervoltage level 2 alarm"}
1790 | 簇 3 充电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2331 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitVoltageDifferenceExcessiveLevel2Alarm | {"en":"Cluster 3 Charging Unit Voltage Difference Excessive Level 2 Alarm"}
1791 | 簇 3 放电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2332 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellPressureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 3 discharge cell pressure difference is too large, level 2 alarm"}
1792 | 簇 3 充电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2333 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingClusterTotalVoltageOverLevel2Alarm | {"en":"Cluster 3 Charging Cluster Total Voltage Over Level 2 Alarm"}
1793 | 簇 3 放电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2334 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeClusterTotalVoltageExceedsLevel2Alarm | {"en":"Cluster 3 discharge cluster total voltage exceeds level 2 alarm"}
1794 | 簇 3 充电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2335 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingClusterTotalVoltageLowLevel2Alarm | {"en":"Cluster 3 Charging Cluster Total Voltage Low Level 2 Alarm"}
1795 | 簇 3 放电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2336 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeClusterTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 3 discharge cluster total voltage too low level 2 alarm"}
1796 | 簇 3 充电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2337 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitHighTemperatureLevel2Alarm | {"en":"Cluster 3 Charging Unit High Temperature Level 2 Alarm"}
1797 | 簇 3 放电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2338 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeUnitHighTemperatureSecondaryAlarm | {"en":"Cluster 3 discharge unit high temperature secondary alarm"}
1798 | 簇 3 充电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2339 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitLowTemperatureLevel2Alarm | {"en":"Cluster 3 charging unit low temperature level 2 alarm"}
1799 | 簇 3 放电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2340 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellLowTemperatureSecondaryAlarm | {"en":"Cluster 3 discharge cell low temperature secondary alarm"}
1800 | 簇 3 充电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2341 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitLevel2AlarmForExcessiveTemperatureDifference | {"en":"Cluster 3 Charging Unit: Level 2 Alarm for Excessive Temperature Difference"}
1801 | 簇 3 放电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2342 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeUnitTemperatureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 3 discharge unit temperature difference is too large, level 2 alarm"}
1802 | 簇 3 充电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2343 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingPackageRoomTotalVoltageDifferenceTooHighLevel2Alarm | {"en":"Cluster 3 Charging Package Room Total Voltage Difference Too High Level 2 Alarm"}
1803 | 簇 3 放电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2344 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForExcessiveTotalPressureDifferenceBetweenDischargePacketsInCluster3 | {"en":"Secondary alarm for excessive total pressure difference between discharge packets in cluster 3"}
1804 | 簇 3 充电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2345 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingPackTotalVoltageOverLevel2Alarm | {"en":"Cluster 3 Charging Pack Total Voltage Over Level 2 Alarm"}
1805 | 簇 3 放电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2346 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargePackageTotalVoltageExceedsLevel2Alarm | {"en":"Cluster 3 discharge package total voltage exceeds level 2 alarm"}
1806 | 簇 3 充电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2347 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingPackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 3 Charging Pack Total Voltage Too Low Level 2 Alarm"}
1807 | 簇 3 放电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2348 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargePackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 3 discharge pack total voltage too low level 2 alarm"}
1808 | 簇 3 充电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2349 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3Level2AlarmForExcessiveChargingCurrent | {"en":"Cluster 3: Level 2 alarm for excessive charging current"}
1809 | 簇 3 放电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2350 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCurrentTooHighLevel2Alarm | {"en":"Cluster 3 discharge current too high level 2 alarm"}
1810 | 簇 3 绝缘过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2351 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3InsulationLowLevel2Alarm | {"en":"Cluster 3 insulation low level 2 alarm"}
1811 | 簇 3 SOC过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2353 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3SocLowLevel2Alarm | {"en":"Cluster 3 SOC Low Level 2 Alarm"}
1812 | 簇 3 充电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2354 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitOvervoltageLevel3Warning | {"en":"Cluster 3 Charging Unit Overvoltage Level 3 Warning"}
1813 | 簇 3 放电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2355 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellOvervoltageLevelThreeWarning | {"en":"Cluster 3 discharge cell overvoltage level three warning"}
1814 | 簇 3 充电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2356 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitUndervoltageLevel3Warning | {"en":"Cluster 3 Charging Unit Undervoltage Level 3 Warning"}
1815 | 簇 3 放电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2357 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellUndervoltageThreeLevelWarning | {"en":"Cluster 3 discharge cell undervoltage three-level warning"}
1816 | 簇 3 充电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2358 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3Level3WarningForExcessiveVoltageDifferenceInChargingCells | {"en":"Cluster 3: Level 3 Warning for Excessive Voltage Difference in Charging Cells"}
1817 | 簇 3 放电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2359 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ThreeLevelWarningForExcessiveDischargeCellPressureDifference | {"en":"Cluster 3: Three level warning for excessive discharge cell pressure difference"}
1818 | 簇 3 充电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2360 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingClusterTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 3 Charging Cluster Total Voltage Over High Level Three Warning"}
1819 | 簇 3 放电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2361 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeClusterTotalPressureHighThreeLevelWarning | {"en":"Cluster 3 discharge cluster total pressure high three level warning"}
1820 | 簇 3 充电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2362 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingClusterTotalVoltageLowLevelThreeWarning | {"en":"Cluster 3 Charging Cluster Total Voltage Low Level Three Warning"}
1821 | 簇 3 放电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2363 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeClusterTotalPressureTooLowThreeLevelWarning | {"en":"Cluster 3 discharge cluster total pressure too low three-level warning"}
1822 | 簇 3 充电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2364 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 3 Charging Unit High Temperature Level Three Warning"}
1823 | 簇 3 放电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2365 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 3 discharge unit high temperature level three warning"}
1824 | 簇 3 充电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2366 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitLowTemperatureLevelThreeWarning | {"en":"Cluster 3 Charging Unit Low Temperature Level Three Warning"}
1825 | 簇 3 放电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2367 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeCellLowTemperatureThreeLevelWarning | {"en":"Cluster 3 discharge cell low temperature three-level warning"}
1826 | 簇 3 充电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2368 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingUnitLevel3WarningForExcessiveTemperatureDifference | {"en":"Cluster 3 Charging Unit: Level 3 Warning for Excessive Temperature Difference"}
1827 | 簇 3 放电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2369 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargeUnitTemperatureDifferenceIsTooLargeLevel3Warning | {"en":"Cluster 3 discharge unit temperature difference is too large, level 3 warning"}
1828 | 簇 3 充电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2370 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ThreeLevelWarningForExcessiveTotalVoltageDifferenceBetweenChargingBags | {"en":"Cluster 3: Three level warning for excessive total voltage difference between charging bags"}
1829 | 簇 3 放电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2371 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ThreeLevelWarningForExcessiveTotalPressureDifferenceBetweenDischargePackets | {"en":"Cluster 3: Three level warning for excessive total pressure difference between discharge packets"}
1830 | 簇 3 充电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2372 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingPackTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 3 Charging Pack Total Voltage Over High Level Three Warning"}
1831 | 簇 3 放电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2373 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargePackageTotalPressureHighThreeLevelWarning | {"en":"Cluster 3 discharge package total pressure high three level warning"}
1832 | 簇 3 充电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2374 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ChargingPackTotalVoltageLowLevelThreeWarning | {"en":"Cluster 3 Charging Pack Total Voltage Low Level Three Warning"}
1833 | 簇 3 放电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2375 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3DischargePackageTotalPressureTooLowLevel3Warning | {"en":"Cluster 3 discharge package total pressure too low Level 3 warning"}
1834 | 簇 3 充电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2376 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3Level3WarningForExcessiveChargingCurrent | {"en":"Cluster 3: Level 3 warning for excessive charging current"}
1835 | 簇 3 放电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2377 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ThreeLevelWarningForExcessiveDischargeCurrent | {"en":"Cluster 3: Three level warning for excessive discharge current"}
1836 | 簇 3 绝缘过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2378 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3InsulationLowLevelThreeWarning | {"en":"Cluster 3 Insulation Low Level Three Warning"}
1837 | 簇 3 SOC过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2380 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3SocLowLevelThreeWarning | {"en":"Cluster 3 SOC Low Level Three Warning"}
1838 | 簇 3 温升告警 | bool |  | 0：系统正常 1：一级预警 | 2381 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3TemperatureRiseAlarm | {"en":"Cluster 3 temperature rise alarm"}
1839 | 簇 3 BCMU序列号异常预警 | bool |  | 0：系统正常 1：一级预警 | 2382 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3BcmuSerialNumberAbnormalWarning | {"en":"Cluster 3 BCMU serial number abnormal warning"}
1840 | 簇 3 簇间压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2383 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3ThreeLevelWarningForExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 3: Three level warning for excessive pressure difference between clusters"}
1841 | 簇 3 二级SD卡异常 | bool |  | 0：系统正常 1：一级预警 | 2384 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3Level2SdCardException | {"en":"Cluster 3 Level 2 SD Card Exception"}
1842 | 簇 3 电磁阀控制模块通讯异常 | bool |  | 0：正常 1：电磁阀模块通讯异常（一级预警） | 2385 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3SolenoidValveControlModuleCommunicationAbnormality | {"en":"Cluster 3 solenoid valve control module communication abnormality"}
1843 | 簇 3 系统故障下电 | bool |  | 0：正常 1：下发故障（三级故障） | 2386 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3SystemFailurePowerOff | {"en":"Cluster 3 system failure power off"}
1844 | 簇 3 BCMU校时反馈 | bool |  | 0：正常 1：已较时 | 2387 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster3BcmuTimingFeedback | {"en":"Cluster 3 BCMU timing feedback"}
1845 | 簇 4 簇启用/停用状态 | bool |  | 0：停用 1：启用 | 2388 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4EnableDisableStatus | {"en":"Cluster 4: Enable/Disable Status"}
1846 | 簇 4 簇充电状态 | bool |  | 0：空闲 1：充电 | 2389 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingStatus | {"en":"Cluster 4 charging status"}
1847 | 簇 4 簇放电状态 | bool |  | 0：空闲 1：放电 | 2390 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeState | {"en":"Cluster 4 discharge state"}
1848 | 簇 4 簇一级故障 | bool |  | 0：系统正常 1：三级故障 | 2391 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ClusterFirstLevelFault | {"en":"Cluster 4 cluster first level fault"}
1849 | 簇 4 簇二级告警 | bool |  | 0：系统正常 1：二级告警 | 2392 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ClusterLevel2Alarm | {"en":"Cluster 4 Cluster Level 2 Alarm"}
1850 | 簇 4 簇三级预警 | bool |  | 0：系统正常 1：一级预警 | 2393 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ClusterLevel3Warning | {"en":"Cluster 4 Cluster Level 3 Warning"}
1851 | 簇 4 簇禁充标志 | bool |  | 0：允许 1：禁止充电 | 2394 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ForbiddenChargingFlag | {"en":"Cluster 4: Forbidden Charging Flag"}
1852 | 簇 4 簇禁放标志 | bool |  | 0：允许 1：禁止放电 | 2395 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ForbiddenSigns | {"en":"Cluster 4: Forbidden Signs"}
1853 | 簇 4 总正接触器状态 | bool |  | 0：断开 1：闭合 | 2396 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4TotalPositiveContactorStatus | {"en":"Cluster 4 total positive contactor status"}
1854 | 簇 4 总负接触器状态 | bool |  | 0：断开 1：闭合 | 2397 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4TotalNegativeContactorStatus | {"en":"Cluster 4 total negative contactor status"}
1855 | 簇 4 预充接触器状态 | bool |  | 0：断开 1：闭合 | 2398 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4PreChargingContactorStatus | {"en":"Cluster 4 Pre charging Contactor Status"}
1856 | 簇 4 运行灯接触器状态 | bool |  | 0：断开 1：闭合 | 2400 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4RunningLightContactorStatus | {"en":"Cluster 4 running light contactor status"}
1857 | 簇 4 故障灯接触器状态 | bool |  | 0：断开 1：闭合 | 2401 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4FaultLightContactorStatus | {"en":"Cluster 4 fault light contactor status"}
1858 | 簇 4 高压箱断路器/隔离开关状态 | bool |  | 0：断开 1：闭合 | 2402 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4HighVoltageBoxCircuitBreakerIsolationSwitchStatus | {"en":"Cluster 4 High Voltage Box Circuit Breaker/Isolation Switch Status"}
1859 | 簇 4 接触器总状态 | bool |  | 0：断开 1：闭合 | 2403 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ContactorOverallStatus | {"en":"Cluster 4 contactor overall status"}
1860 | 簇 4 总正接触器粘连 | bool |  | 0：正常 1：三级故障 | 2404 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4TotalPositiveContactorAdhesion | {"en":"Cluster 4 total positive contactor adhesion"}
1861 | 簇 4 总负接触器粘连 | bool |  | 0：正常 1：三级故障 | 2405 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4TotalNegativeContactorAdhesion | {"en":"Cluster 4 total negative contactor adhesion"}
1862 | 簇 4 总正接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2407 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4TotalPositiveContactorStuck | {"en":"Cluster 4 total positive contactor stuck"}
1863 | 簇 4 总负接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2408 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4TotalNegativeContactorStuck | {"en":"Cluster 4 total negative contactor stuck"}
1864 | 簇 4 单体电压采集故障 | bool |  | 0：正常 1：三级故障 | 2413 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4SingleCellVoltageAcquisitionFault | {"en":"Cluster 4 single cell voltage acquisition fault"}
1865 | 簇 4 单体温度采集故障 | bool |  | 0：正常 1：三级故障 | 2414 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4MonomerTemperatureAcquisitionFault | {"en":"Cluster 4 monomer temperature acquisition fault"}
1866 | 簇 4 INCAN接收异常 | bool |  | 0：正常 1：三级故障 | 2416 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4IncanReceivingException | {"en":"Cluster 4 INCAN receiving exception"}
1867 | 簇 4 BMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2417 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4BmuCommunicationFailure | {"en":"Cluster 4 BMU communication failure"}
1868 | 簇 4 BAMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2418 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4BamuCommunicationFailure | {"en":"Cluster 4 BAMU communication failure"}
1869 | 簇 4 充电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2420 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitOvervoltageLevel1Fault | {"en":"Cluster 4 charging unit overvoltage level 1 fault"}
1870 | 簇 4 放电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2421 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellOvervoltageLevel1Fault | {"en":"Cluster 4 discharge cell overvoltage level 1 fault"}
1871 | 簇 4 充电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2422 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitUndervoltageLevel1Fault | {"en":"Cluster 4 charging unit undervoltage level 1 fault"}
1872 | 簇 4 放电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2423 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellUndervoltagePrimaryFault | {"en":"Cluster 4 discharge cell undervoltage primary fault"}
1873 | 簇 4 充电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2424 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 4 charging unit voltage difference is too large, first level fault"}
1874 | 簇 4 放电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2425 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 4 discharge cell voltage difference is too large, first level fault"}
1875 | 簇 4 充电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2426 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingClusterTotalVoltageHighLevelOneFault | {"en":"Cluster 4 Charging Cluster Total Voltage High Level One Fault"}
1876 | 簇 4 放电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2427 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeClusterTotalVoltageTooHighLevelOneFault | {"en":"Cluster 4 discharge cluster total voltage too high level one fault"}
1877 | 簇 4 充电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2428 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 4 Charging Cluster Total Voltage Too Low Level One Fault"}
1878 | 簇 4 放电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2429 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 4 discharge cluster total voltage too low level one fault"}
1879 | 簇 4 充电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2430 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitHighTemperatureFirstLevelFault | {"en":"Cluster 4 charging unit high temperature first level fault"}
1880 | 簇 4 放电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2431 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeUnitHighTemperaturePrimaryFault | {"en":"Cluster 4 discharge unit high temperature primary fault"}
1881 | 簇 4 充电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2432 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitLowTemperatureLevelOneFault | {"en":"Cluster 4 charging unit low temperature level one fault"}
1882 | 簇 4 放电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2433 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellLowTemperaturePrimaryFault | {"en":"Cluster 4 discharge cell low-temperature primary fault"}
1883 | 簇 4 充电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2434 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 4 charging unit temperature difference is too large, level 1 fault"}
1884 | 簇 4 放电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2435 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 4 discharge unit temperature difference is too large, level 1 fault"}
1885 | 簇 4 充电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2436 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingPackageRoomTotalVoltageDifferenceTooLargeLevelOneFault | {"en":"Cluster 4 Charging Package Room Total Voltage Difference Too Large Level One Fault"}
1886 | 簇 4 放电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2437 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargePacketHasAFirstLevelFaultDueToExcessiveTotalPressureDifferenceBetweenTheDischargePackets | {"en":"Cluster 4 discharge packet has a first level fault due to excessive total pressure difference between the discharge packets"}
1887 | 簇 4 充电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2438 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingPackTotalVoltageHighLevelOneFault | {"en":"Cluster 4 Charging Pack Total Voltage High Level One Fault"}
1888 | 簇 4 放电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2439 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargePacketTotalVoltageTooHighLevelOneFault | {"en":"Cluster 4 discharge packet total voltage too high level one fault"}
1889 | 簇 4 充电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2440 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingPackTotalVoltageTooLowLevelOneFault | {"en":"Cluster 4 Charging Pack Total Voltage Too Low Level One Fault"}
1890 | 簇 4 放电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2441 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargePacketTotalVoltageTooLowLevelOneFault | {"en":"Cluster 4 discharge packet total voltage too low level one fault"}
1891 | 簇 4 充电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2442 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingCurrentTooHighLevelOneFault | {"en":"Cluster 4 charging current too high level one fault"}
1892 | 簇 4 放电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2443 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCurrentTooHighLevelOneFault | {"en":"Cluster 4 discharge current too high level one fault"}
1893 | 簇 4 绝缘过低一级故障 | bool |  | 0：正常 1：三级故障 | 2444 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4InsulationLowLevelOneFault | {"en":"Cluster 4 insulation low level one fault"}
1894 | 簇 4 SOC过低一级故障 | bool |  | 0：正常 1：三级故障 | 2446 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4SocLowLevelOneFault | {"en":"Cluster 4 SOC low level one fault"}
1895 | 簇 4 热失控故障 | bool |  | 0：正常 1：三级故障 | 2447 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ThermalRunawayFault | {"en":"Cluster 4 thermal runaway fault"}
1896 | 簇 4 电流采集故障 | bool |  | 0：正常 1：三级故障 | 2448 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4CurrentAcquisitionFault | {"en":"Cluster 4 current acquisition fault"}
1897 | 簇 4 簇内压差过大故障 | bool |  | 0：正常 1：三级故障 | 2449 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4FaultOfExcessivePressureDifferenceWithinCluster | {"en":"Cluster 4: Fault of excessive pressure difference within cluster"}
1898 | 簇 4 簇间压差过大故障 | bool |  | 0：正常 1：三级故障 | 2450 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4FaultOfExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 4: Fault of excessive pressure difference between clusters"}
1899 | 簇 4 管路漏液故障 | bool |  | 0：正常 1：三级故障 | 2451 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4PipelineLeakageFault | {"en":"Cluster 4 pipeline leakage fault"}
1900 | 簇 4 极柱温度采集故障 | bool |  | 0：正常 1：三级故障 | 2452 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4PoleTemperatureAcquisitionFault | {"en":"Cluster 4 pole temperature acquisition fault"}
1901 | 簇 4 充电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2456 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitOvervoltageLevel2Alarm | {"en":"Cluster 4 charging unit overvoltage level 2 alarm"}
1902 | 簇 4 放电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2457 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellOvervoltageLevel2Alarm | {"en":"Cluster 4 discharge cell overvoltage level 2 alarm"}
1903 | 簇 4 充电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2458 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitUndervoltageLevel2Alarm | {"en":"Cluster 4 charging unit undervoltage level 2 alarm"}
1904 | 簇 4 放电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2459 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellUndervoltageLevel2Alarm | {"en":"Cluster 4 discharge cell undervoltage level 2 alarm"}
1905 | 簇 4 充电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2460 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitVoltageDifferenceExcessiveLevel2Alarm | {"en":"Cluster 4 Charging Unit Voltage Difference Excessive Level 2 Alarm"}
1906 | 簇 4 放电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2461 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellPressureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 4 discharge cell pressure difference is too large, level 2 alarm"}
1907 | 簇 4 充电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2462 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingClusterTotalVoltageOverLevel2Alarm | {"en":"Cluster 4 Charging Cluster Total Voltage Over Level 2 Alarm"}
1908 | 簇 4 放电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2463 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeClusterTotalVoltageOverHighLevel2Alarm | {"en":"Cluster 4 discharge cluster total voltage over high level 2 alarm"}
1909 | 簇 4 充电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2464 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingClusterTotalVoltageLowLevel2Alarm | {"en":"Cluster 4 Charging Cluster Total Voltage Low Level 2 Alarm"}
1910 | 簇 4 放电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2465 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeClusterTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 4 discharge cluster total voltage too low level 2 alarm"}
1911 | 簇 4 充电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2466 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitHighTemperatureLevel2Alarm | {"en":"Cluster 4 Charging Unit High Temperature Level 2 Alarm"}
1912 | 簇 4 放电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2467 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeUnitHighTemperatureSecondaryAlarm | {"en":"Cluster 4 discharge unit high temperature secondary alarm"}
1913 | 簇 4 充电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2468 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitLowTemperatureLevel2Alarm | {"en":"Cluster 4 charging unit low temperature level 2 alarm"}
1914 | 簇 4 放电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2469 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellLowTemperatureSecondaryAlarm | {"en":"Cluster 4 discharge cell low temperature secondary alarm"}
1915 | 簇 4 充电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2470 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitLevel2AlarmForExcessiveTemperatureDifference | {"en":"Cluster 4 Charging Unit: Level 2 Alarm for Excessive Temperature Difference"}
1916 | 簇 4 放电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2471 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeUnitTemperatureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 4 discharge unit temperature difference is too large, level 2 alarm"}
1917 | 簇 4 充电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2472 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingPackageRoomTotalVoltageDifferenceTooHighLevel2Alarm | {"en":"Cluster 4 Charging Package Room Total Voltage Difference Too High Level 2 Alarm"}
1918 | 簇 4 放电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2473 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForExcessiveTotalPressureDifferenceBetweenCluster4DischargePackets | {"en":"Secondary alarm for excessive total pressure difference between cluster 4 discharge packets"}
1919 | 簇 4 充电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2474 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingPackTotalVoltageOverLevel2Alarm | {"en":"Cluster 4 Charging Pack Total Voltage Over Level 2 Alarm"}
1920 | 簇 4 放电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2475 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargePackTotalVoltageHighLevel2Alarm | {"en":"Cluster 4 discharge pack total voltage high level 2 alarm"}
1921 | 簇 4 充电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2476 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingPackTotalVoltageLowLevel2Alarm | {"en":"Cluster 4 Charging Pack Total Voltage Low Level 2 Alarm"}
1922 | 簇 4 放电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2477 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargePackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 4 discharge pack total voltage too low level 2 alarm"}
1923 | 簇 4 充电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2478 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4Level2AlarmForExcessiveChargingCurrent | {"en":"Cluster 4: Level 2 alarm for excessive charging current"}
1924 | 簇 4 放电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2479 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCurrentTooHighLevel2Alarm | {"en":"Cluster 4 discharge current too high level 2 alarm"}
1925 | 簇 4 绝缘过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2480 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4InsulationLowLevel2Alarm | {"en":"Cluster 4 insulation low level 2 alarm"}
1926 | 簇 4 SOC过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2482 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4SocLowLevel2Alarm | {"en":"Cluster 4 SOC Low Level 2 Alarm"}
1927 | 簇 4 充电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2483 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitOvervoltageLevel3Warning | {"en":"Cluster 4 Charging Unit Overvoltage Level 3 Warning"}
1928 | 簇 4 放电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2484 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellOvervoltageThreeLevelWarning | {"en":"Cluster 4 discharge cell overvoltage three-level warning"}
1929 | 簇 4 充电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2485 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitUndervoltageLevel3Warning | {"en":"Cluster 4 Charging Unit Undervoltage Level 3 Warning"}
1930 | 簇 4 放电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2486 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellUndervoltageThreeLevelWarning | {"en":"Cluster 4 discharge cell undervoltage three-level warning"}
1931 | 簇 4 充电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2487 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ThreeLevelWarningForExcessiveVoltageDifferenceInChargingCells | {"en":"Cluster 4: Three level warning for excessive voltage difference in charging cells"}
1932 | 簇 4 放电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2488 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ThreeLevelWarningForExcessiveDischargeCellPressureDifference | {"en":"Cluster 4: Three level warning for excessive discharge cell pressure difference"}
1933 | 簇 4 充电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2489 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingClusterTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 4 Charging Cluster Total Voltage Over High Level Three Warning"}
1934 | 簇 4 放电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2490 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeClusterTotalPressureHighThreeLevelWarning | {"en":"Cluster 4 discharge cluster total pressure high three level warning"}
1935 | 簇 4 充电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2491 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingClusterTotalVoltageLowLevelThreeWarning | {"en":"Cluster 4 Charging Cluster Total Voltage Low Level Three Warning"}
1936 | 簇 4 放电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2492 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeClusterTotalVoltageLowThreeLevelWarning | {"en":"Cluster 4 discharge cluster total voltage low three-level warning"}
1937 | 簇 4 充电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2493 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 4 Charging Unit High Temperature Level Three Warning"}
1938 | 簇 4 放电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2494 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 4 discharge unit high temperature level three warning"}
1939 | 簇 4 充电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2495 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitLowTemperatureLevelThreeWarning | {"en":"Cluster 4 Charging Unit Low Temperature Level Three Warning"}
1940 | 簇 4 放电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2496 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeCellLowTemperatureThreeLevelWarning | {"en":"Cluster 4 discharge cell low temperature three-level warning"}
1941 | 簇 4 充电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2497 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingUnitLevel3WarningForExcessiveTemperatureDifference | {"en":"Cluster 4 Charging Unit: Level 3 Warning for Excessive Temperature Difference"}
1942 | 簇 4 放电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2498 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargeUnitTemperatureDifferenceIsTooLargeLevel3Warning | {"en":"Cluster 4 discharge unit temperature difference is too large, level 3 warning"}
1943 | 簇 4 充电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2499 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ThreeLevelWarningForExcessiveTotalVoltageDifferenceBetweenChargingBags | {"en":"Cluster 4: Three level warning for excessive total voltage difference between charging bags"}
1944 | 簇 4 放电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2500 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ThreeLevelWarningForExcessiveTotalPressureDifferenceBetweenDischargePackets | {"en":"Cluster 4: Three level warning for excessive total pressure difference between discharge packets"}
1945 | 簇 4 充电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2501 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingPackTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 4 Charging Pack Total Voltage Over High Level Three Warning"}
1946 | 簇 4 放电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2502 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargePackageTotalPressureHighThreeLevelWarning | {"en":"Cluster 4 discharge package total pressure high three level warning"}
1947 | 簇 4 充电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2503 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ChargingPackTotalVoltageLowLevelThreeWarning | {"en":"Cluster 4 Charging Pack Total Voltage Low Level Three Warning"}
1948 | 簇 4 放电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2504 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4DischargePackageTotalVoltageLowLevelThreeWarning | {"en":"Cluster 4 discharge package total voltage low level three warning"}
1949 | 簇 4 充电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2505 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4Level3WarningForExcessiveChargingCurrent | {"en":"Cluster 4: Level 3 warning for excessive charging current"}
1950 | 簇 4 放电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2506 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ThreeLevelWarningForExcessiveDischargeCurrent | {"en":"Cluster 4: Three level warning for excessive discharge current"}
1951 | 簇 4 绝缘过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2507 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4InsulationLowLevelThreeWarning | {"en":"Cluster 4 Insulation Low Level Three Warning"}
1952 | 簇 4 SOC过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2509 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4SocLowLevelThreeWarning | {"en":"Cluster 4 SOC Low Level Three Warning"}
1953 | 簇 4 温升告警 | bool |  | 0：系统正常 1：一级预警 | 2510 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4TemperatureRiseAlarm | {"en":"Cluster 4 temperature rise alarm"}
1954 | 簇 4 BCMU序列号异常预警 | bool |  | 0：系统正常 1：一级预警 | 2511 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4BcmuSerialNumberAnomalyWarning | {"en":"Cluster 4 BCMU serial number anomaly warning"}
1955 | 簇 4 簇间压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2512 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4ThreeLevelWarningForExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 4: Three level warning for excessive pressure difference between clusters"}
1956 | 簇 4 二级SD卡异常 | bool |  | 0：系统正常 1：一级预警 | 2513 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4Level2SdCardException | {"en":"Cluster 4 Level 2 SD Card Exception"}
1957 | 簇 4 电磁阀控制模块通讯异常 | bool |  | 0：正常 1：电磁阀模块通讯异常（一级预警） | 2514 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4SolenoidValveControlModuleCommunicationAbnormality | {"en":"Cluster 4 solenoid valve control module communication abnormality"}
1958 | 簇 4 系统故障下电 | bool |  | 0：正常 1：下发故障（三级故障） | 2515 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4SystemFailurePowerOff | {"en":"Cluster 4 system failure power off"}
1959 | 簇 4 BCMU校时反馈 | bool |  | 0：正常 1：已较时 | 2516 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster4BcmuTimingFeedback | {"en":"Cluster 4 BCMU timing feedback"}
1960 | 簇 5 簇启用/停用状态 | bool |  | 0：停用 1：启用 | 2517 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5EnableDisableStatus | {"en":"Cluster 5: Enable/Disable Status"}
1961 | 簇 5 簇充电状态 | bool |  | 0：空闲 1：充电 | 2518 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingStatus | {"en":"Cluster 5 charging status"}
1962 | 簇 5 簇放电状态 | bool |  | 0：空闲 1：放电 | 2519 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeState | {"en":"Cluster 5 discharge state"}
1963 | 簇 5 簇一级故障 | bool |  | 0：系统正常 1：三级故障 | 2520 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ClusterFirstLevelFault | {"en":"Cluster 5 cluster first level fault"}
1964 | 簇 5 簇二级告警 | bool |  | 0：系统正常 1：二级告警 | 2521 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ClusterLevel2Alarm | {"en":"Cluster 5 Cluster Level 2 Alarm"}
1965 | 簇 5 簇三级预警 | bool |  | 0：系统正常 1：一级预警 | 2522 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ClusterLevel3Warning | {"en":"Cluster 5 Cluster Level 3 Warning"}
1966 | 簇 5 簇禁充标志 | bool |  | 0：允许 1：禁止充电 | 2523 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ForbiddenChargingFlag | {"en":"Cluster 5: Forbidden Charging Flag"}
1967 | 簇 5 簇禁放标志 | bool |  | 0：允许 1：禁止放电 | 2524 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ForbiddenSigns | {"en":"Cluster 5: Forbidden Signs"}
1968 | 簇 5 总正接触器状态 | bool |  | 0：断开 1：闭合 | 2525 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5TotalPositiveContactorStatus | {"en":"Cluster 5 total positive contactor status"}
1969 | 簇 5 总负接触器状态 | bool |  | 0：断开 1：闭合 | 2526 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5TotalNegativeContactorStatus | {"en":"Cluster 5 total negative contactor status"}
1970 | 簇 5 预充接触器状态 | bool |  | 0：断开 1：闭合 | 2527 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5PreChargingContactorStatus | {"en":"Cluster 5 Pre charging Contactor Status"}
1971 | 簇 5 运行灯接触器状态 | bool |  | 0：断开 1：闭合 | 2529 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5RunningLightContactorStatus | {"en":"Cluster 5 running light contactor status"}
1972 | 簇 5 故障灯接触器状态 | bool |  | 0：断开 1：闭合 | 2530 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5FaultLightContactorStatus | {"en":"Cluster 5 fault light contactor status"}
1973 | 簇 5 高压箱断路器/隔离开关状态 | bool |  | 0：断开 1：闭合 | 2531 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5HighVoltageBoxCircuitBreakerIsolationSwitchStatus | {"en":"Cluster 5 High Voltage Box Circuit Breaker/Isolation Switch Status"}
1974 | 簇 5 接触器总状态 | bool |  | 0：断开 1：闭合 | 2532 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ContactorOverallStatus | {"en":"Cluster 5 contactor overall status"}
1975 | 簇 5 总正接触器粘连 | bool |  | 0：正常 1：三级故障 | 2533 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5TotalPositiveContactorAdhesion | {"en":"Cluster 5 total positive contactor adhesion"}
1976 | 簇 5 总负接触器粘连 | bool |  | 0：正常 1：三级故障 | 2534 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5TotalNegativeContactorAdhesion | {"en":"Cluster 5 total negative contactor adhesion"}
1977 | 簇 5 总正接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2536 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5TotalPositiveContactorStuck | {"en":"Cluster 5 total positive contactor stuck"}
1978 | 簇 5 总负接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2537 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5TotalNegativeContactorStuck | {"en":"Cluster 5 total negative contactor stuck"}
1979 | 簇 5 单体电压采集故障 | bool |  | 0：正常 1：三级故障 | 2542 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5SingleCellVoltageAcquisitionFault | {"en":"Cluster 5 single cell voltage acquisition fault"}
1980 | 簇 5 单体温度采集故障 | bool |  | 0：正常 1：三级故障 | 2543 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5MonomerTemperatureAcquisitionFault | {"en":"Cluster 5 monomer temperature acquisition fault"}
1981 | 簇 5 INCAN接收异常 | bool |  | 0：正常 1：三级故障 | 2545 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5IncanReceivingException | {"en":"Cluster 5 INCAN receiving exception"}
1982 | 簇 5 BMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2546 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5BmuCommunicationFailure | {"en":"Cluster 5 BMU communication failure"}
1983 | 簇 5 BAMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2547 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5BamuCommunicationFailure | {"en":"Cluster 5 BAMU communication failure"}
1984 | 簇 5 充电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2549 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitOvervoltageLevel1Fault | {"en":"Cluster 5 charging unit overvoltage level 1 fault"}
1985 | 簇 5 放电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2550 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeUnitOvervoltageLevel1Fault | {"en":"Cluster 5 discharge unit overvoltage level 1 fault"}
1986 | 簇 5 充电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2551 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitUndervoltageLevel1Fault | {"en":"Cluster 5 charging unit undervoltage level 1 fault"}
1987 | 簇 5 放电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2552 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellUndervoltagePrimaryFault | {"en":"Cluster 5 discharge cell undervoltage primary fault"}
1988 | 簇 5 充电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2553 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 5 charging unit voltage difference is too large, first level fault"}
1989 | 簇 5 放电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2554 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 5 discharge cell voltage difference is too large, first level fault"}
1990 | 簇 5 充电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2555 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingClusterTotalVoltageHighLevelOneFault | {"en":"Cluster 5 Charging Cluster Total Voltage High Level One Fault"}
1991 | 簇 5 放电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2556 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeClusterTotalVoltageTooHighLevelOneFault | {"en":"Cluster 5 discharge cluster total voltage too high level one fault"}
1992 | 簇 5 充电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2557 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 5 Charging Cluster Total Voltage Too Low Level One Fault"}
1993 | 簇 5 放电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2558 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 5 discharge cluster total voltage too low level one fault"}
1994 | 簇 5 充电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2559 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitHighTemperatureFirstLevelFault | {"en":"Cluster 5 charging unit high temperature first level fault"}
1995 | 簇 5 放电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2560 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeUnitHighTemperaturePrimaryFault | {"en":"Cluster 5 discharge unit high temperature primary fault"}
1996 | 簇 5 充电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2561 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitLowTemperatureLevelOneFault | {"en":"Cluster 5 charging unit low temperature level one fault"}
1997 | 簇 5 放电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2562 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeUnitLowTemperaturePrimaryFault | {"en":"Cluster 5 discharge unit low-temperature primary fault"}
1998 | 簇 5 充电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2563 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 5 charging unit temperature difference is too large, level 1 fault"}
1999 | 簇 5 放电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2564 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 5 discharge unit temperature difference is too large, level 1 fault"}
2000 | 簇 5 充电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2565 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingPackageRoomTotalVoltageDifferenceTooLargeLevelOneFault | {"en":"Cluster 5 Charging Package Room Total Voltage Difference Too Large Level One Fault"}
2001 | 簇 5 放电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2566 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargePacketHasAFirstLevelFaultDueToExcessiveTotalPressureDifferenceBetweenTheDischargePackets | {"en":"Cluster 5 discharge packet has a first level fault due to excessive total pressure difference between the discharge packets"}
2002 | 簇 5 充电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2567 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingPackTotalVoltageHighLevelOneFault | {"en":"Cluster 5 Charging Pack Total Voltage High Level One Fault"}
2003 | 簇 5 放电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2568 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargePackTotalVoltageTooHighLevelOneFault | {"en":"Cluster 5 discharge pack total voltage too high level one fault"}
2004 | 簇 5 充电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2569 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingPackTotalVoltageTooLowLevelOneFault | {"en":"Cluster 5 Charging Pack Total Voltage Too Low Level One Fault"}
2005 | 簇 5 放电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2570 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargePacketTotalVoltageTooLowLevelOneFault | {"en":"Cluster 5 discharge packet total voltage too low level one fault"}
2006 | 簇 5 充电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2571 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingCurrentTooHighLevelOneFault | {"en":"Cluster 5 charging current too high level one fault"}
2007 | 簇 5 放电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2572 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCurrentTooHighLevelOneFault | {"en":"Cluster 5 discharge current too high level one fault"}
2008 | 簇 5 绝缘过低一级故障 | bool |  | 0：正常 1：三级故障 | 2573 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5InsulationLowLevelOneFault | {"en":"Cluster 5 insulation low level one fault"}
2009 | 簇 5 SOC过低一级故障 | bool |  | 0：正常 1：三级故障 | 2575 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5SocLowLevelOneFault | {"en":"Cluster 5 SOC low level one fault"}
2010 | 簇 5 热失控故障 | bool |  | 0：正常 1：三级故障 | 2576 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ThermalRunawayFault | {"en":"Cluster 5 thermal runaway fault"}
2011 | 簇 5 电流采集故障 | bool |  | 0：正常 1：三级故障 | 2577 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5CurrentAcquisitionFault | {"en":"Cluster 5 current acquisition fault"}
2012 | 簇 5 簇内压差过大故障 | bool |  | 0：正常 1：三级故障 | 2578 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5FaultOfExcessivePressureDifferenceWithinCluster | {"en":"Cluster 5: Fault of excessive pressure difference within cluster"}
2013 | 簇 5 簇间压差过大故障 | bool |  | 0：正常 1：三级故障 | 2579 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5FaultOfExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 5: Fault of excessive pressure difference between clusters"}
2014 | 簇 5 管路漏液故障 | bool |  | 0：正常 1：三级故障 | 2580 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5PipelineLeakageFault | {"en":"Cluster 5 pipeline leakage fault"}
2015 | 簇 5 极柱温度采集故障 | bool |  | 0：正常 1：三级故障 | 2581 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5PoleTemperatureAcquisitionFault | {"en":"Cluster 5 pole temperature acquisition fault"}
2016 | 簇 5 充电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2585 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitOvervoltageLevel2Alarm | {"en":"Cluster 5 charging unit overvoltage level 2 alarm"}
2017 | 簇 5 放电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2586 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellOvervoltageLevel2Alarm | {"en":"Cluster 5 discharge cell overvoltage level 2 alarm"}
2018 | 簇 5 充电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2587 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitUndervoltageLevel2Alarm | {"en":"Cluster 5 charging unit undervoltage level 2 alarm"}
2019 | 簇 5 放电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2588 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellUndervoltageLevel2Alarm | {"en":"Cluster 5 discharge cell undervoltage level 2 alarm"}
2020 | 簇 5 充电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2589 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitVoltageDifferenceExcessiveLevel2Alarm | {"en":"Cluster 5 Charging Unit Voltage Difference Excessive Level 2 Alarm"}
2021 | 簇 5 放电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2590 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellPressureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 5 discharge cell pressure difference is too large, level 2 alarm"}
2022 | 簇 5 充电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2591 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingClusterTotalVoltageOverLevel2Alarm | {"en":"Cluster 5 Charging Cluster Total Voltage Over Level 2 Alarm"}
2023 | 簇 5 放电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2592 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeClusterTotalVoltageHighSecondaryAlarm | {"en":"Cluster 5 discharge cluster total voltage high secondary alarm"}
2024 | 簇 5 充电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2593 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingClusterTotalVoltageLowLevel2Alarm | {"en":"Cluster 5 Charging Cluster Total Voltage Low Level 2 Alarm"}
2025 | 簇 5 放电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2594 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeClusterTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 5 discharge cluster total voltage too low level 2 alarm"}
2026 | 簇 5 充电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2595 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitHighTemperatureLevel2Alarm | {"en":"Cluster 5 Charging Unit High Temperature Level 2 Alarm"}
2027 | 簇 5 放电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2596 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeUnitHighTemperatureSecondaryAlarm | {"en":"Cluster 5 discharge unit high temperature secondary alarm"}
2028 | 簇 5 充电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2597 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitLowTemperatureLevel2Alarm | {"en":"Cluster 5 charging unit low temperature level 2 alarm"}
2029 | 簇 5 放电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2598 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellLowTemperatureSecondaryAlarm | {"en":"Cluster 5 discharge cell low temperature secondary alarm"}
2030 | 簇 5 充电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2599 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitLevel2AlarmForExcessiveTemperatureDifference | {"en":"Cluster 5 Charging Unit: Level 2 Alarm for Excessive Temperature Difference"}
2031 | 簇 5 放电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2600 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeUnitTemperatureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 5 discharge unit temperature difference is too large, level 2 alarm"}
2032 | 簇 5 充电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2601 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingPackageRoomTotalVoltageDifferenceTooHighLevel2Alarm | {"en":"Cluster 5 Charging Package Room Total Voltage Difference Too High Level 2 Alarm"}
2033 | 簇 5 放电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2602 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5SecondaryAlarmForExcessiveTotalPressureDifferenceBetweenDischargePackets | {"en":"Cluster 5: Secondary alarm for excessive total pressure difference between discharge packets"}
2034 | 簇 5 充电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2603 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingPackTotalVoltageOverLevel2Alarm | {"en":"Cluster 5 Charging Pack Total Voltage Over Level 2 Alarm"}
2035 | 簇 5 放电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2604 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargePackTotalVoltageHighLevel2Alarm | {"en":"Cluster 5 discharge pack total voltage high level 2 alarm"}
2036 | 簇 5 充电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2605 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingPackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 5 Charging Pack Total Voltage Too Low Level 2 Alarm"}
2037 | 簇 5 放电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2606 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargePackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 5 discharge pack total voltage too low level 2 alarm"}
2038 | 簇 5 充电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2607 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5Level2AlarmForExcessiveChargingCurrent | {"en":"Cluster 5: Level 2 alarm for excessive charging current"}
2039 | 簇 5 放电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2608 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5Level2AlarmForExcessiveDischargeCurrent | {"en":"Cluster 5: Level 2 alarm for excessive discharge current"}
2040 | 簇 5 绝缘过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2609 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5InsulationLowLevel2Alarm | {"en":"Cluster 5 insulation low level 2 alarm"}
2041 | 簇 5 SOC过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2611 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5SocLowSecondLevelAlarm | {"en":"Cluster 5 SOC low second level alarm"}
2042 | 簇 5 充电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2612 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitOvervoltageLevel3Warning | {"en":"Cluster 5 Charging Unit Overvoltage Level 3 Warning"}
2043 | 簇 5 放电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2613 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellOvervoltageLevelThreeWarning | {"en":"Cluster 5 discharge cell overvoltage level three warning"}
2044 | 簇 5 充电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2614 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitUndervoltageLevel3Warning | {"en":"Cluster 5 Charging Unit Undervoltage Level 3 Warning"}
2045 | 簇 5 放电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2615 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellUndervoltageThreeLevelWarning | {"en":"Cluster 5 discharge cell undervoltage three-level warning"}
2046 | 簇 5 充电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2616 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ThreeLevelWarningForExcessiveVoltageDifferenceInChargingCells | {"en":"Cluster 5: Three level warning for excessive voltage difference in charging cells"}
2047 | 簇 5 放电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2617 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ThreeLevelWarningForExcessiveDischargeCellPressureDifference | {"en":"Cluster 5: Three level warning for excessive discharge cell pressure difference"}
2048 | 簇 5 充电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2618 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingClusterTotalVoltageHighLevelThreeWarning | {"en":"Cluster 5 Charging Cluster Total Voltage High Level Three Warning"}
2049 | 簇 5 放电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2619 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeClusterTotalPressureHighThreeLevelWarning | {"en":"Cluster 5 discharge cluster total pressure high three level warning"}
2050 | 簇 5 充电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2620 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingClusterTotalVoltageLowLevelThreeWarning | {"en":"Cluster 5 Charging Cluster Total Voltage Low Level Three Warning"}
2051 | 簇 5 放电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2621 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeClusterTotalVoltageTooLowThreeLevelWarning | {"en":"Cluster 5 discharge cluster total voltage too low three-level warning"}
2052 | 簇 5 充电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2622 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 5 Charging Unit High Temperature Level Three Warning"}
2053 | 簇 5 放电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2623 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 5 discharge unit high temperature level three warning"}
2054 | 簇 5 充电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2624 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitLowTemperatureLevelThreeWarning | {"en":"Cluster 5 Charging Unit Low Temperature Level Three Warning"}
2055 | 簇 5 放电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2625 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeCellLowTemperatureThreeLevelWarning | {"en":"Cluster 5 discharge cell low temperature three-level warning"}
2056 | 簇 5 充电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2626 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingUnitLevel3WarningForExcessiveTemperatureDifference | {"en":"Cluster 5 Charging Unit: Level 3 Warning for Excessive Temperature Difference"}
2057 | 簇 5 放电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2627 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargeUnitTemperatureDifferenceIsTooLargeLevel3Warning | {"en":"Cluster 5 discharge unit temperature difference is too large, level 3 warning"}
2058 | 簇 5 充电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2628 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ThreeLevelWarningForExcessiveTotalVoltageDifferenceBetweenChargingBags | {"en":"Cluster 5: Three level warning for excessive total voltage difference between charging bags"}
2059 | 簇 5 放电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2629 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ThreeLevelWarningForExcessiveTotalPressureDifferenceBetweenDischargePackets | {"en":"Cluster 5: Three level warning for excessive total pressure difference between discharge packets"}
2060 | 簇 5 充电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2630 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingPackTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 5 Charging Pack Total Voltage Over High Level Three Warning"}
2061 | 簇 5 放电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2631 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargePackageTotalPressureHighThreeLevelWarning | {"en":"Cluster 5 discharge package total pressure high three level warning"}
2062 | 簇 5 充电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2632 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ChargingPackTotalVoltageLowLevelThreeWarning | {"en":"Cluster 5 Charging Pack Total Voltage Low Level Three Warning"}
2063 | 簇 5 放电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2633 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5DischargePackageTotalVoltageLowLevelThreeWarning | {"en":"Cluster 5 discharge package total voltage low level three warning"}
2064 | 簇 5 充电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2634 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5Level3WarningForExcessiveChargingCurrent | {"en":"Cluster 5: Level 3 warning for excessive charging current"}
2065 | 簇 5 放电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2635 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ThreeLevelWarningForExcessiveDischargeCurrent | {"en":"Cluster 5: Three level warning for excessive discharge current"}
2066 | 簇 5 绝缘过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2636 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5InsulationLowLevelThreeWarning | {"en":"Cluster 5 insulation low level three warning"}
2067 | 簇 5 SOC过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2638 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5SocLowLevelThreeWarning | {"en":"Cluster 5 SOC Low Level Three Warning"}
2068 | 簇 5 温升告警 | bool |  | 0：系统正常 1：一级预警 | 2639 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5TemperatureRiseAlarm | {"en":"Cluster 5 temperature rise alarm"}
2069 | 簇 5 BCMU序列号异常预警 | bool |  | 0：系统正常 1：一级预警 | 2640 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5BcmuSerialNumberAbnormalWarning | {"en":"Cluster 5 BCMU serial number abnormal warning"}
2070 | 簇 5 簇间压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2641 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5ThreeLevelWarningForExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 5: Three level warning for excessive pressure difference between clusters"}
2071 | 簇 5 二级SD卡异常 | bool |  | 0：系统正常 1：一级预警 | 2642 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5Level2SdCardException | {"en":"Cluster 5 Level 2 SD Card Exception"}
2072 | 簇 5 电磁阀控制模块通讯异常 | bool |  | 0：正常 1：电磁阀模块通讯异常（一级预警） | 2643 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5SolenoidValveControlModuleCommunicationAbnormality | {"en":"Cluster 5 solenoid valve control module communication abnormality"}
2073 | 簇 5 系统故障下电 | bool |  | 0：正常 1：下发故障（三级故障） | 2644 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5SystemFailurePowerOff | {"en":"Cluster 5 system failure power off"}
2074 | 簇 5 BCMU校时反馈 | bool |  | 0：正常 1：已较时 | 2645 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster5BcmuTimingFeedback | {"en":"Cluster 5 BCMU timing feedback"}
2075 | 簇 6 簇启用/停用状态 | bool |  | 0：停用 1：启用 | 2646 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6EnableDisableStatus | {"en":"Cluster 6: Enable/Disable Status"}
2076 | 簇 6 簇充电状态 | bool |  | 0：空闲 1：充电 | 2647 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingStatus | {"en":"Cluster 6 charging status"}
2077 | 簇 6 簇放电状态 | bool |  | 0：空闲 1：放电 | 2648 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeState | {"en":"Cluster 6 discharge state"}
2078 | 簇 6 簇一级故障 | bool |  | 0：系统正常 1：三级故障 | 2649 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ClusterFirstLevelFault | {"en":"Cluster 6 cluster first level fault"}
2079 | 簇 6 簇二级告警 | bool |  | 0：系统正常 1：二级告警 | 2650 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ClusterLevel2Alarm | {"en":"Cluster 6 Cluster Level 2 Alarm"}
2080 | 簇 6 簇三级预警 | bool |  | 0：系统正常 1：一级预警 | 2651 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ClusterLevel3Warning | {"en":"Cluster 6 Cluster Level 3 Warning"}
2081 | 簇 6 簇禁充标志 | bool |  | 0：允许 1：禁止充电 | 2652 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ClusterNoChargingFlag | {"en":"Cluster 6 cluster no charging flag"}
2082 | 簇 6 簇禁放标志 | bool |  | 0：允许 1：禁止放电 | 2653 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ForbiddenSigns | {"en":"Cluster 6: Forbidden Signs"}
2083 | 簇 6 总正接触器状态 | bool |  | 0：断开 1：闭合 | 2654 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6TotalPositiveContactorStatus | {"en":"Cluster 6 total positive contactor status"}
2084 | 簇 6 总负接触器状态 | bool |  | 0：断开 1：闭合 | 2655 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6TotalNegativeContactorStatus | {"en":"Cluster 6 total negative contactor status"}
2085 | 簇 6 预充接触器状态 | bool |  | 0：断开 1：闭合 | 2656 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6PreChargingContactorStatus | {"en":"Cluster 6 Pre charging Contactor Status"}
2086 | 簇 6 运行灯接触器状态 | bool |  | 0：断开 1：闭合 | 2658 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6RunningLightContactorStatus | {"en":"Cluster 6 running light contactor status"}
2087 | 簇 6 故障灯接触器状态 | bool |  | 0：断开 1：闭合 | 2659 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6FaultLightContactorStatus | {"en":"Cluster 6 fault light contactor status"}
2088 | 簇 6 高压箱断路器/隔离开关状态 | bool |  | 0：断开 1：闭合 | 2660 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6HighVoltageBoxCircuitBreakerIsolationSwitchStatus | {"en":"Cluster 6 High Voltage Box Circuit Breaker/Isolation Switch Status"}
2089 | 簇 6 接触器总状态 | bool |  | 0：断开 1：闭合 | 2661 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ContactorOverallStatus | {"en":"Cluster 6 contactor overall status"}
2090 | 簇 6 总正接触器粘连 | bool |  | 0：正常 1：三级故障 | 2662 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6TotalPositiveContactorAdhesion | {"en":"Cluster 6 total positive contactor adhesion"}
2091 | 簇 6 总负接触器粘连 | bool |  | 0：正常 1：三级故障 | 2663 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6TotalNegativeContactorAdhesion | {"en":"Cluster 6 total negative contactor adhesion"}
2092 | 簇 6 总正接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2665 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6PositiveContactorStuck | {"en":"Cluster 6 positive contactor stuck"}
2093 | 簇 6 总负接触器卡滞 | bool |  | 0：正常 1：三级故障 | 2666 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6TotalNegativeContactorStuck | {"en":"Cluster 6 total negative contactor stuck"}
2094 | 簇 6 单体电压采集故障 | bool |  | 0：正常 1：三级故障 | 2671 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6SingleCellVoltageAcquisitionFault | {"en":"Cluster 6 single cell voltage acquisition fault"}
2095 | 簇 6 单体温度采集故障 | bool |  | 0：正常 1：三级故障 | 2672 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6MonomerTemperatureAcquisitionFault | {"en":"Cluster 6 monomer temperature acquisition fault"}
2096 | 簇 6 INCAN接收异常 | bool |  | 0：正常 1：三级故障 | 2674 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6IncanReceivingException | {"en":"Cluster 6 INCAN receiving exception"}
2097 | 簇 6 BMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2675 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6BmuCommunicationFailure | {"en":"Cluster 6 BMU communication failure"}
2098 | 簇 6 BAMU通讯故障 | bool |  | 0：正常 1：三级故障 | 2676 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6BamuCommunicationFailure | {"en":"Cluster 6 BAMU communication failure"}
2099 | 簇 6 充电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2678 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitOvervoltageLevel1Fault | {"en":"Cluster 6 charging unit overvoltage level 1 fault"}
2100 | 簇 6 放电单体过压一级故障 | bool |  | 0：正常 1：三级故障 | 2679 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeUnitOvervoltageLevel1Fault | {"en":"Cluster 6 discharge unit overvoltage level 1 fault"}
2101 | 簇 6 充电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2680 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitUndervoltageLevelOneFault | {"en":"Cluster 6 charging unit undervoltage level one fault"}
2102 | 簇 6 放电单体欠压一级故障 | bool |  | 0：正常 1：三级故障 | 2681 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellUndervoltagePrimaryFault | {"en":"Cluster 6 discharge cell undervoltage primary fault"}
2103 | 簇 6 充电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2682 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 6 charging unit voltage difference is too large, first level fault"}
2104 | 簇 6 放电单体压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2683 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellVoltageDifferenceIsTooLargeFirstLevelFault | {"en":"Cluster 6 discharge cell voltage difference is too large, first level fault"}
2105 | 簇 6 充电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2684 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingClusterTotalVoltageHighLevelOneFault | {"en":"Cluster 6 Charging Cluster Total Voltage High Level One Fault"}
2106 | 簇 6 放电簇总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2685 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeClusterTotalVoltageTooHighLevelOneFault | {"en":"Cluster 6 discharge cluster total voltage too high level one fault"}
2107 | 簇 6 充电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2686 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 6 Charging Cluster Total Voltage Too Low Level One Fault"}
2108 | 簇 6 放电簇总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2687 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeClusterTotalVoltageTooLowLevelOneFault | {"en":"Cluster 6 discharge cluster total voltage too low level one fault"}
2109 | 簇 6 充电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2688 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitHighTemperatureFirstLevelFault | {"en":"Cluster 6 charging unit high temperature first level fault"}
2110 | 簇 6 放电单体高温一级故障 | bool |  | 0：正常 1：三级故障 | 2689 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeUnitHighTemperaturePrimaryFault | {"en":"Cluster 6 discharge unit high temperature primary fault"}
2111 | 簇 6 充电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2690 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitLowTemperatureLevelOneFault | {"en":"Cluster 6 charging unit low temperature level one fault"}
2112 | 簇 6 放电单体低温一级故障 | bool |  | 0：正常 1：三级故障 | 2691 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellLowTemperaturePrimaryFault | {"en":"Cluster 6 discharge cell low-temperature primary fault"}
2113 | 簇 6 充电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2692 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 6 charging unit temperature difference is too large, level 1 fault"}
2114 | 簇 6 放电单体温差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2693 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeUnitTemperatureDifferenceIsTooLargeLevel1Fault | {"en":"Cluster 6 discharge unit temperature difference is too large, level 1 fault"}
2115 | 簇 6 充电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2694 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingPackageRoomTotalVoltageDifferenceTooLargeLevelOneFault | {"en":"Cluster 6 Charging Package Room Total Voltage Difference Too Large Level One Fault"}
2116 | 簇 6 放电包间总压压差过大一级故障 | bool |  | 0：正常 1：三级故障 | 2695 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargePacketHasAFirstLevelFaultDueToExcessiveTotalPressureDifferenceBetweenTheDischargePackets | {"en":"Cluster 6 discharge packet has a first level fault due to excessive total pressure difference between the discharge packets"}
2117 | 簇 6 充电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2696 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingPackTotalVoltageHighLevelOneFault | {"en":"Cluster 6 Charging Pack Total Voltage High Level One Fault"}
2118 | 簇 6 放电包总压过高一级故障 | bool |  | 0：正常 1：三级故障 | 2697 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargePackTotalVoltageTooHighLevelOneFault | {"en":"Cluster 6 discharge pack total voltage too high level one fault"}
2119 | 簇 6 充电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2698 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingPackTotalVoltageTooLowLevelOneFault | {"en":"Cluster 6 Charging Pack Total Voltage Too Low Level One Fault"}
2120 | 簇 6 放电包总压过低一级故障 | bool |  | 0：正常 1：三级故障 | 2699 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargePackTotalVoltageTooLowLevelOneFault | {"en":"Cluster 6 discharge pack total voltage too low level one fault"}
2121 | 簇 6 充电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2700 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingCurrentTooHighLevelOneFault | {"en":"Cluster 6 charging current too high level one fault"}
2122 | 簇 6 放电电流过大一级故障 | bool |  | 0：正常 1：三级故障 | 2701 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCurrentTooHighLevelOneFault | {"en":"Cluster 6 discharge current too high level one fault"}
2123 | 簇 6 绝缘过低一级故障 | bool |  | 0：正常 1：三级故障 | 2702 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6InsulationLowLevelOneFault | {"en":"Cluster 6 insulation low level one fault"}
2124 | 簇 6 SOC过低一级故障 | bool |  | 0：正常 1：三级故障 | 2704 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6SocLowLevelOneFault | {"en":"Cluster 6 SOC low level one fault"}
2125 | 簇 6 热失控故障 | bool |  | 0：正常 1：三级故障 | 2705 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ThermalRunawayFault | {"en":"Cluster 6 thermal runaway fault"}
2126 | 簇 6 电流采集故障 | bool |  | 0：正常 1：三级故障 | 2706 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6CurrentAcquisitionFault | {"en":"Cluster 6 current acquisition fault"}
2127 | 簇 6 簇内压差过大故障 | bool |  | 0：正常 1：三级故障 | 2707 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6FaultOfExcessivePressureDifferenceWithinCluster | {"en":"Cluster 6: Fault of excessive pressure difference within cluster"}
2128 | 簇 6 簇间压差过大故障 | bool |  | 0：正常 1：三级故障 | 2708 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6FaultOfExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 6: Fault of excessive pressure difference between clusters"}
2129 | 簇 6 管路漏液故障 | bool |  | 0：正常 1：三级故障 | 2709 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6PipelineLeakageFault | {"en":"Cluster 6 pipeline leakage fault"}
2130 | 簇 6 极柱温度采集故障 | bool |  | 0：正常 1：三级故障 | 2710 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6PoleTemperatureAcquisitionFault | {"en":"Cluster 6 pole temperature acquisition fault"}
2131 | 簇 6 充电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2714 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitOvervoltageLevel2Alarm | {"en":"Cluster 6 charging unit overvoltage level 2 alarm"}
2132 | 簇 6 放电单体过压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2715 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellOvervoltageLevel2Alarm | {"en":"Cluster 6 discharge cell overvoltage level 2 alarm"}
2133 | 簇 6 充电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2716 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitUndervoltageLevel2Alarm | {"en":"Cluster 6 charging unit undervoltage level 2 alarm"}
2134 | 簇 6 放电单体欠压二级告警 | bool |  | 0：系统正常 1：二级告警 | 2717 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellUndervoltageLevel2Alarm | {"en":"Cluster 6 discharge cell undervoltage level 2 alarm"}
2135 | 簇 6 充电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2718 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitVoltageDifferenceExcessiveLevel2Alarm | {"en":"Cluster 6 Charging Unit Voltage Difference Excessive Level 2 Alarm"}
2136 | 簇 6 放电单体压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2719 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellPressureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 6 discharge cell pressure difference is too large, level 2 alarm"}
2137 | 簇 6 充电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2720 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingClusterTotalVoltageOverLevel2Alarm | {"en":"Cluster 6 Charging Cluster Total Voltage Over Level 2 Alarm"}
2138 | 簇 6 放电簇总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2721 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeClusterTotalVoltageHighSecondaryAlarm | {"en":"Cluster 6 discharge cluster total voltage high secondary alarm"}
2139 | 簇 6 充电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2722 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingClusterTotalVoltageLowLevel2Alarm | {"en":"Cluster 6 Charging Cluster Total Voltage Low Level 2 Alarm"}
2140 | 簇 6 放电簇总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2723 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeClusterTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 6 discharge cluster total voltage too low level 2 alarm"}
2141 | 簇 6 充电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2724 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitHighTemperatureLevel2Alarm | {"en":"Cluster 6 Charging Unit High Temperature Level 2 Alarm"}
2142 | 簇 6 放电单体高温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2725 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeUnitHighTemperatureSecondaryAlarm | {"en":"Cluster 6 discharge unit high temperature secondary alarm"}
2143 | 簇 6 充电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2726 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitLowTemperatureLevel2Alarm | {"en":"Cluster 6 charging unit low temperature level 2 alarm"}
2144 | 簇 6 放电单体低温二级告警 | bool |  | 0：系统正常 1：二级告警 | 2727 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellLowTemperatureSecondaryAlarm | {"en":"Cluster 6 discharge cell low temperature secondary alarm"}
2145 | 簇 6 充电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2728 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitLevel2AlarmForExcessiveTemperatureDifference | {"en":"Cluster 6 Charging Unit: Level 2 Alarm for Excessive Temperature Difference"}
2146 | 簇 6 放电单体温差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2729 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeUnitTemperatureDifferenceIsTooLargeLevel2Alarm | {"en":"Cluster 6 discharge unit temperature difference is too large, level 2 alarm"}
2147 | 簇 6 充电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2730 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingPackageRoomTotalVoltageDifferenceTooHighLevel2Alarm | {"en":"Cluster 6 Charging Package Room Total Voltage Difference Too High Level 2 Alarm"}
2148 | 簇 6 放电包间总压压差过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2731 | DiscreteInputs | 1 | AB | 1 | 0 |  | secondaryAlarmForExcessiveTotalPressureDifferenceBetweenCluster6DischargePackets | {"en":"Secondary alarm for excessive total pressure difference between cluster 6 discharge packets"}
2149 | 簇 6 充电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2732 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingPackTotalVoltageOverLevel2Alarm | {"en":"Cluster 6 Charging Pack Total Voltage Over Level 2 Alarm"}
2150 | 簇 6 放电包总压过高二级告警 | bool |  | 0：系统正常 1：二级告警 | 2733 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargePackTotalVoltageHighLevel2Alarm | {"en":"Cluster 6 discharge pack total voltage high level 2 alarm"}
2151 | 簇 6 充电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2734 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingPackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 6 Charging Pack Total Voltage Too Low Level 2 Alarm"}
2152 | 簇 6 放电包总压过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2735 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargePackTotalVoltageTooLowLevel2Alarm | {"en":"Cluster 6 discharge pack total voltage too low level 2 alarm"}
2153 | 簇 6 充电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2736 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6Level2AlarmForExcessiveChargingCurrent | {"en":"Cluster 6: Level 2 alarm for excessive charging current"}
2154 | 簇 6 放电电流过大二级告警 | bool |  | 0：系统正常 1：二级告警 | 2737 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCurrentTooHighLevel2Alarm | {"en":"Cluster 6 discharge current too high level 2 alarm"}
2155 | 簇 6 绝缘过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2738 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6InsulationLowLevel2Alarm | {"en":"Cluster 6 insulation low level 2 alarm"}
2156 | 簇 6 SOC过低二级告警 | bool |  | 0：系统正常 1：二级告警 | 2740 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6SocLowLevel2Alarm | {"en":"Cluster 6 SOC Low Level 2 Alarm"}
2157 | 簇 6 充电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2741 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitOvervoltageLevel3Warning | {"en":"Cluster 6 Charging Unit Overvoltage Level 3 Warning"}
2158 | 簇 6 放电单体过压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2742 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellOvervoltageLevelThreeWarning | {"en":"Cluster 6 discharge cell overvoltage level three warning"}
2159 | 簇 6 充电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2743 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitUndervoltageLevel3Warning | {"en":"Cluster 6 Charging Unit Undervoltage Level 3 Warning"}
2160 | 簇 6 放电单体欠压三级预警 | bool |  | 0：系统正常 1：一级预警 | 2744 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellUndervoltageThreeLevelWarning | {"en":"Cluster 6 discharge cell undervoltage three-level warning"}
2161 | 簇 6 充电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2745 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ThreeLevelWarningForExcessiveVoltageDifferenceInChargingCells | {"en":"Cluster 6: Three level warning for excessive voltage difference in charging cells"}
2162 | 簇 6 放电单体压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2746 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ThreeLevelWarningForExcessiveDischargeCellPressureDifference | {"en":"Cluster 6: Three level warning for excessive discharge cell pressure difference"}
2163 | 簇 6 充电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2747 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingClusterTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 6 Charging Cluster Total Voltage Over High Level Three Warning"}
2164 | 簇 6 放电簇总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2748 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeClusterTotalPressureHighThreeLevelWarning | {"en":"Cluster 6 discharge cluster total pressure high three level warning"}
2165 | 簇 6 充电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2749 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingClusterTotalVoltageLowLevelThreeWarning | {"en":"Cluster 6 Charging Cluster Total Voltage Low Level Three Warning"}
2166 | 簇 6 放电簇总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2750 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeClusterTotalVoltageTooLowThreeLevelWarning | {"en":"Cluster 6 discharge cluster total voltage too low three-level warning"}
2167 | 簇 6 充电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2751 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 6 Charging Unit High Temperature Level Three Warning"}
2168 | 簇 6 放电单体高温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2752 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeUnitHighTemperatureLevelThreeWarning | {"en":"Cluster 6 discharge unit high temperature level three warning"}
2169 | 簇 6 充电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2753 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitLowTemperatureLevelThreeWarning | {"en":"Cluster 6 Charging Unit Low Temperature Level Three Warning"}
2170 | 簇 6 放电单体低温三级预警 | bool |  | 0：系统正常 1：一级预警 | 2754 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeCellLowTemperatureThreeLevelWarning | {"en":"Cluster 6 discharge cell low temperature three-level warning"}
2171 | 簇 6 充电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2755 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingUnitLevel3WarningForExcessiveTemperatureDifference | {"en":"Cluster 6 Charging Unit: Level 3 Warning for Excessive Temperature Difference"}
2172 | 簇 6 放电单体温差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2756 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargeUnitTemperatureDifferenceIsTooLargeLevel3Warning | {"en":"Cluster 6 discharge unit temperature difference is too large, level 3 warning"}
2173 | 簇 6 充电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2757 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ThreeLevelWarningForExcessiveTotalVoltageDifferenceBetweenChargingBags | {"en":"Cluster 6: Three level warning for excessive total voltage difference between charging bags"}
2174 | 簇 6 放电包间总压压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2758 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ThreeLevelWarningForExcessiveTotalPressureDifferenceBetweenDischargePackets | {"en":"Cluster 6: Three level warning for excessive total pressure difference between discharge packets"}
2175 | 簇 6 充电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2759 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingPackTotalVoltageOverHighLevelThreeWarning | {"en":"Cluster 6 Charging Pack Total Voltage Over High Level Three Warning"}
2176 | 簇 6 放电包总压过高三级预警 | bool |  | 0：系统正常 1：一级预警 | 2760 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargePackageHighTotalPressureWarningLevel3 | {"en":"Cluster 6 discharge package high total pressure warning level 3"}
2177 | 簇 6 充电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2761 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ChargingPackTotalVoltageLowLevelThreeWarning | {"en":"Cluster 6 Charging Pack Total Voltage Low Level Three Warning"}
2178 | 簇 6 放电包总压过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2762 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6DischargePackageTotalVoltageTooLowLevel3Warning | {"en":"Cluster 6 discharge package total voltage too low Level 3 warning"}
2179 | 簇 6 充电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2763 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6Level3WarningForExcessiveChargingCurrent | {"en":"Cluster 6: Level 3 warning for excessive charging current"}
2180 | 簇 6 放电电流过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2764 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ThreeLevelWarningForExcessiveDischargeCurrent | {"en":"Cluster 6: Three level warning for excessive discharge current"}
2181 | 簇 6 绝缘过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2765 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6InsulationLowLevelThreeWarning | {"en":"Cluster 6 insulation low level three warning"}
2182 | 簇 6 SOC过低三级预警 | bool |  | 0：系统正常 1：一级预警 | 2767 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6SocLowLevelThreeWarning | {"en":"Cluster 6 SOC Low Level Three Warning"}
2183 | 簇 6 温升告警 | bool |  | 0：系统正常 1：一级预警 | 2768 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6TemperatureRiseAlarm | {"en":"Cluster 6 temperature rise alarm"}
2184 | 簇 6 BCMU序列号异常预警 | bool |  | 0：系统正常 1：一级预警 | 2769 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6BcmuSerialNumberAbnormalWarning | {"en":"Cluster 6 BCMU serial number abnormal warning"}
2185 | 簇 6 簇间压差过大三级预警 | bool |  | 0：系统正常 1：一级预警 | 2770 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6ThreeLevelWarningForExcessivePressureDifferenceBetweenClusters | {"en":"Cluster 6: Three level warning for excessive pressure difference between clusters"}
2186 | 簇 6 二级SD卡异常 | bool |  | 0：系统正常 1：一级预警 | 2771 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6Level2SdCardException | {"en":"Cluster 6 Level 2 SD Card Exception"}
2187 | 簇 6 电磁阀控制模块通讯异常 | bool |  | 0：正常 1：电磁阀模块通讯异常（一级预警） | 2772 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6SolenoidValveControlModuleCommunicationAbnormality | {"en":"Cluster 6 solenoid valve control module communication abnormality"}
2188 | 簇 6 系统故障下电 | bool |  | 0：正常 1：下发故障（三级故障） | 2773 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6SystemFailurePowerOff | {"en":"Cluster 6 system failure power off"}
2189 | 簇 6 BCMU校时反馈 | bool |  | 0：正常 1：已较时 | 2774 | DiscreteInputs | 1 | AB | 1 | 0 |  | cluster6BcmuTimingFeedback | {"en":"Cluster 6 BCMU timing feedback"}