## iec104
id | key | name | ca | ioa | type | scale | offset | unit | enable | trans | status_words | warn_bits | level | note
1 | gridFrequency | 电网频率 | 1 | 0 | yc | 0.01 | 0 | HZ |  | {"en":"GridFrequency"}
2 | lineVoltageAB | 系统线电压AB | 1 | 1 | yc | 0.1 | 0 | V |  | {"en":"LineVoltageAB"}
3 | lineVoltageBC | 系统线电压BC | 1 | 2 | yc | 0.1 | 0 | V |  | {"en":"LineVoltageBC"}
4 | lineVoltageCA | 系统线电压CA | 1 | 3 | yc | 0.1 | 0 | V |  | {"en":"LineVoltageCA"}
5 | currentA | 系统电流A | 1 | 4 | yc | 0.1 | 0 | A |  | {"en":"CurrentA"}
6 | currentB | 系统电流B | 1 | 5 | yc | 0.1 | 0 | A |  | {"en":"CurrentB"}
7 | currentC | 系统电流C | 1 | 6 | yc | 0.1 | 0 | A |  | {"en":"CurrentC"}
8 | dcVoltageTypical | 直流电压典型值 | 1 | 7 | yc | 0.1 | 0 | V |  | {"en":"DcVoltageTypical"}
9 | dcTotalCurrent | 直流总电流 | 1 | 8 | yc | 0.1 | 0 | A |  | {"en":"DcTotalCurrent"}
10 | dcTotalPower | 直流总功率 | 1 | 9 | yc | 0.1 | 0 | kW |  | {"en":"DcTotalPower"}
11 | totalPowerFactor | 总功率因数 | 1 | 10 | yc | 0.001 | 0 |  |  | {"en":"TotalPowerFactor"}
12 | totalApparentPower | 总视在功率 | 1 | 11 | yc | 0.1 | 0 | kVA |  | {"en":"TotalApparentPower"}
13 | pcsActivePower | PCS实时有功功率 | 1 | 12 | yc | 0.1 | 0 | KW |  | {"en":"PcsActivePower"}
14 | pcsReactivePower | PCS实时无功功率 | 1 | 13 | yc | 0.1 | 0 | KVAR |  | {"en":"PcsReactivePower"}
15 | dailyChargeEnergy | 累计日充电量 | 1 | 14 | yc | 0.1 | 0 | kW·h |  | {"en":"DailyChargeEnergy"}
16 | dailyDischargeEnergy | 累计日放电量 | 1 | 15 | yc | 0.1 | 0 | kW·h |  | {"en":"DailyDischargeEnergy"}
17 | totalChargeEnergy | 系统累计充电量 | 1 | 16 | yc | 0.1 | 0 | kW·h |  | {"en":"TotalChargeEnergy"}
18 | totalDischargeEnergy | 系统累计放电量 | 1 | 17 | yc | 0.1 | 0 | kW·h |  | {"en":"TotalDischargeEnergy"}
19 | pcsMaxChargeActivePower | PCS最大可充有功功率 | 1 | 18 | yc | 0.1 | 0 | kW |  | {"en":"PcsMaxChargeActivePower"}
20 | pcsMaxDischargeActivePower | PCS最大可放有功功率 | 1 | 19 | yc | 0.1 | 0 | kW |  | {"en":"PcsMaxDischargeActivePower"}
21 | pcsMaxCapacitiveReactivePower | PCS最大可用容性无功功率 | 1 | 20 | yc | 0.1 | 0 | kVar |  | {"en":"PcsMaxCapacitiveReactivePower"}
22 | pcsMaxInductiveReactivePower | PCS最大可用感性无功功率 | 1 | 21 | yc | 0.1 | 0 | kVar |  | {"en":"PcsMaxInductiveReactivePower"}
23 | soc | SOC | 1 | 22 | yc | 0.1 | 0 | % |  | {"en":"Soc"}
24 | soh | SOH | 1 | 23 | yc | 0.1 | 0 | % |  | {"en":"Soh"}
25 | gridVoltageUnbalance | 电网电压不平衡度 | 1 | 24 | yc | 1 | 0 |  |  | {"en":"GridVoltageUnbalance"}
26 | outputVoltageUnbalance | 输出电压不平衡度 | 1 | 25 | yc | 1 | 0 |  |  | {"en":"OutputVoltageUnbalance"}
27 | outputCurrentUnbalance | 输出电流不平衡度 | 1 | 26 | yc | 1 | 0 |  |  | {"en":"OutputCurrentUnbalance"}
28 | pcsIgbtMaxTempSite | PCS IGBT最大温度站点 | 1 | 27 | yc | 1 | 0 |  |  | {"en":"PcsIgbtMaxTempSite"}
29 | pcsIgbtMaxTemp | PCS IGBT最大温度 | 1 | 28 | yc | 0.1 | 0 | ℃ |  | {"en":"PcsIgbtMaxTemp"}
30 | pcsIgbtMinTempSite | PCS IGBT最小温度站点 | 1 | 29 | yc | 1 | 0 |  |  | {"en":"PcsIgbtMinTempSite"}
31 | pcsIgbtMinTemp | PCS IGBT最小温度 | 1 | 30 | yc | 0.1 | 0 | ℃ |  | {"en":"PcsIgbtMinTemp"}
32 | pcsAmbientMaxTempSite | PCS 环境最大温度站点 | 1 | 31 | yc | 1 | 0 |  |  | {"en":"PcsAmbientMaxTempSite"}
33 | pcsAmbientMaxTemp | PCS 环境最大温度 | 1 | 32 | yc | 0.1 | 0 | ℃ |  | {"en":"PcsAmbientMaxTemp"}
34 | pcsAmbientMinTempSite | PCS 环境最小温度站点 | 1 | 33 | yc | 1 | 0 |  |  | {"en":"PcsAmbientMinTempSite"}
35 | pcsAmbientMinTemp | PCS 环境最小温度 | 1 | 34 | yc | 0.1 | 0 | ℃ |  | {"en":"PcsAmbientMinTemp"}
36 | ambientHumidity | 环境湿度 | 1 | 35 | yc | 0.001 | 0 | % |  | {"en":"AmbientHumidity"}
37 | posInsulationMinResSite | 系统正极绝缘电阻最小值站点 | 1 | 36 | yc | 1 | 0 |  |  | {"en":"PosInsulationMinResSite"}
38 | posInsulationMinRes | 系统正极绝缘电阻最小值 | 1 | 37 | yc | 0.1 | 0 | kΩ |  | {"en":"PosInsulationMinRes"}
39 | negInsulationMinResSite | 系统负极绝缘电阻最小值站点 | 1 | 38 | yc | 1 | 0 |  |  | {"en":"NegInsulationMinResSite"}
40 | negInsulationMinRes | 系统负极绝缘电阻最小值 | 1 | 39 | yc | 0.1 | 0 | kΩ |  | {"en":"NegInsulationMinRes"}
41 | powerRegDeadZone | 功率调节死区 | 1 | 40 | yc | 0.1 | 0 | kW |  | {"en":"PowerRegDeadZone"}
42 | socBalanceDeadZone | SOC均衡死区 | 1 | 41 | yc | 0.1 | 0 | % |  | {"en":"SocBalanceDeadZone"}
43 | powerRegPeriod | 功率调节周期 | 1 | 42 | yc | 1 | 0 | ms |  | {"en":"PowerRegPeriod"}
44 | powerRampCoeff | 功率调节速率/功率爬坡系数 | 1 | 43 | yc | 0.1 | 0 | kW/s |  | {"en":"PowerRampCoeff"}
45 | chargeTrickleThreshold | 充电涓流阈值 | 1 | 44 | yc | 0.1 | 0 | % |  | {"en":"ChargeTrickleThreshold"}
46 | dischargeTrickleThreshold | 放电涓流阈值 | 1 | 45 | yc | 0.1 | 0 | % |  | {"en":"DischargeTrickleThreshold"}
47 | sysTimeSec | 系统时间（秒） | 1 | 46 | yc | 1 | 0 |  |  | {"en":"SysTimeSec"}
48 | sysTimeMin | 系统时间（分） | 1 | 47 | yc | 1 | 0 |  |  | {"en":"SysTimeMin"}
49 | sysTimeHour | 系统时间（时） | 1 | 48 | yc | 1 | 0 |  |  | {"en":"SysTimeHour"}
50 | sysTimeDay | 系统时间（日） | 1 | 49 | yc | 1 | 0 |  |  | {"en":"SysTimeDay"}
51 | sysTimeMonth | 系统时间（月） | 1 | 50 | yc | 1 | 0 |  |  | {"en":"SysTimeMonth"}
52 | sysTimeYear | 系统时间（年） | 1 | 51 | yc | 1 | 0 |  |  | {"en":"SysTimeYear"}
53 | subStationAlarm | 子站控制器告警 | 1 | 52 | yc | 1 | 0 |  |  | {"en":"SubStationAlarm"} |  | 通信故障¦Communication fault¦2 DI输入故障¦DI input fault¦2 配置故障¦Configuration fault¦2 液冷机组故障¦Liquid cooling unit fault¦2 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0
54 | ecatEventAlarm | ECAT事件告警 | 1 | 53 | yc | 1 | 0 |  |  | {"en":"EcatEventAlarm"} |  | ECAT开启失败¦EtherCAT startup failed¦2 扫描从站超时¦Slave scan timeout¦2 从站数量不匹配¦Slave count mismatch¦2 期望的从站数量设置错误¦Incorrect expected slave count setting¦2 PDO映射失败¦PDO mapping failed¦2 主站网口断联¦Master network port disconnected¦2 通讯数据异常¦Abnormal communication data¦2 运行是从站丢失¦Slave lost during operation¦2 从站状态机错误¦Slave state machine error¦2 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0 预留¦Reserve¦0
55 | modbusTcpEventAlarm | MODBUS-TCP事件告警 | 1 | 54 | yc | 1 | 0 |  |  | {"en":"ModbusTcpEventAlarm"} |  | PCS1 通信异常¦PCS1 communication abnormal¦2 PCS2 通信异常¦PCS2 communication abnormal¦2 PCS3 通信异常¦PCS3 communication abnormal¦2 PCS4 通信异常¦PCS4 communication abnormal¦2 PCS5 通信异常¦PCS5 communication abnormal¦2 PCS6 通信异常¦PCS6 communication abnormal¦2 PCS7 通信异常¦PCS7 communication abnormal¦2 PCS8 通信异常¦PCS8 communication abnormal¦2 PCS9 通信异常¦PCS9 communication abnormal¦2 PCS10 通信异常¦PCS10 communication abnormal¦2 PCS11 通信异常¦PCS11 communication abnormal¦2 PCS12 通信异常¦PCS12 communication abnormal¦2 PCS13 通信异常¦PCS13 communication abnormal¦2 PCS14 通信异常¦PCS14 communication abnormal¦2 PCS15 通信异常¦PCS15 communication abnormal¦2 PCS16 通信异常¦PCS16 communication abnormal¦2
56 | modbusRtuEventAlarm | MODBUS-RTU事件告警 | 1 | 55 | yc | 1 | 0 |  |  | {"en":"ModbusRtuEventAlarm"} |  | PCS1 通信异常¦PCS1 communication abnormal¦2 PCS2 通信异常¦PCS2 communication abnormal¦2 PCS3 通信异常¦PCS3 communication abnormal¦2 PCS4 通信异常¦PCS4 communication abnormal¦2 PCS5 通信异常¦PCS5 communication abnormal¦2 PCS6 通信异常¦PCS6 communication abnormal¦2 PCS7 通信异常¦PCS7 communication abnormal¦2 PCS8 通信异常¦PCS8 communication abnormal¦2 PCS9 通信异常¦PCS9 communication abnormal¦2 PCS10 通信异常¦PCS10 communication abnormal¦2 PCS11 通信异常¦PCS11 communication abnormal¦2 PCS12 通信异常¦PCS12 communication abnormal¦2 PCS13 通信异常¦PCS13 communication abnormal¦2 PCS14 通信异常¦PCS14 communication abnormal¦2 PCS15 通信异常¦PCS15 communication abnormal¦2 PCS16 通信异常¦PCS16 communication abnormal¦2
57 | sccDiStatus | SCC DI状态 | 1 | 56 | yc | 1 | 0 |  |  | {"en":"SccDiStatus"}
58 | sccDoStatus | SCC DO状态 | 1 | 57 | yc | 1 | 0 |  |  | {"en":"SccDoStatus"}
59 | pcs1FaultCode | PCS1故障码 | 1 | 58 | yc | 1 | 0 |  |  | {"en":"Pcs1FaultCode"}
60 | pcs2FaultCode | PCS2故障码 | 1 | 59 | yc | 1 | 0 |  |  | {"en":"Pcs2FaultCode"}
61 | pcs3FaultCode | PCS3故障码 | 1 | 60 | yc | 1 | 0 |  |  | {"en":"Pcs3FaultCode"}
62 | pcs4FaultCode | PCS4故障码 | 1 | 61 | yc | 1 | 0 |  |  | {"en":"Pcs4FaultCode"}
63 | pcs5FaultCode | PCS5故障码 | 1 | 62 | yc | 1 | 0 |  |  | {"en":"Pcs5FaultCode"}
64 | pcs6FaultCode | PCS6故障码 | 1 | 63 | yc | 1 | 0 |  |  | {"en":"Pcs6FaultCode"}
65 | pcs7FaultCode | PCS7故障码 | 1 | 64 | yc | 1 | 0 |  |  | {"en":"Pcs7FaultCode"}
66 | pcs8FaultCode | PCS8故障码 | 1 | 65 | yc | 1 | 0 |  |  | {"en":"Pcs8FaultCode"}
67 | pcs9FaultCode | PCS9故障码 | 1 | 66 | yc | 1 | 0 |  |  | {"en":"Pcs9FaultCode"}
68 | pcs10FaultCode | PCS10故障码 | 1 | 67 | yc | 1 | 0 |  |  | {"en":"Pcs10FaultCode"}
69 | pcs11FaultCode | PCS11故障码 | 1 | 68 | yc | 1 | 0 |  |  | {"en":"Pcs11FaultCode"}
70 | pcs12FaultCode | PCS12故障码 | 1 | 69 | yc | 1 | 0 |  |  | {"en":"Pcs12FaultCode"}
71 | liquidCoolingFault | 液冷机组故障 | 1 | 70 | yc | 1 | 0 |  |  | {"en":"LiquidCoolingFault"}
72 | sccDiFault | SCC DI故障 | 1 | 71 | yc | 1 | 0 |  |  | {"en":"SccDiFault"}
73 | sccConfigFault | SCC 配置故障 | 1 | 72 | yc | 1 | 0 |  |  | {"en":"SccConfigFault"}
1000 | statusStopped | 工作状态-停机 | 1 | 0 | yx | 1 | 0 |  |  | {"en":"StatusStopped"}
1001 | statusStandby | 工作状态-待机 | 1 | 1 | yx | 1 | 0 |  |  | {"en":"StatusStandby"}
1002 | statusCharging | 工作状态-充电运行 | 1 | 2 | yx | 1 | 0 |  |  | {"en":"StatusCharging"}
1003 | statusDischarging | 工作状态-放电运行 | 1 | 3 | yx | 1 | 0 |  |  | {"en":"StatusDischarging"}
1004 | statusFault | 工作状态-故障 | 1 | 4 | yx | 1 | 0 |  |  | {"en":"StatusFault"}
1005 | statusZeroPower | 工作状态-零功率 | 1 | 5 | yx | 1 | 0 |  |  | {"en":"StatusZeroPower"}
1006 | statusAlarm | 工作状态-告警 | 1 | 6 | yx | 1 | 0 |  |  | {"en":"StatusAlarm"}
1007 | pcsGridMode | PCS并离网状态 | 1 | 7 | yx | 1 | 0 |  |  | {"en":"PcsGridMode"}
1008 | in0Status | IN0状态 | 1 | 8 | yx | 1 | 0 |  |  | {"en":"In0Status"}
1009 | in1Status | IN1状态 | 1 | 9 | yx | 1 | 0 |  |  | {"en":"In1Status"}
1010 | in2Status | IN2状态 | 1 | 10 | yx | 1 | 0 |  |  | {"en":"In2Status"}
1011 | in3Status | IN3状态 | 1 | 11 | yx | 1 | 0 |  |  | {"en":"In3Status"}
1012 | in4Status | IN4状态 | 1 | 12 | yx | 1 | 0 |  |  | {"en":"In4Status"}
1013 | in5Status | IN5状态 | 1 | 13 | yx | 1 | 0 |  |  | {"en":"In5Status"}
1014 | in6Status | IN6状态 | 1 | 14 | yx | 1 | 0 |  |  | {"en":"In6Status"}
1015 | in7Status | IN7状态 | 1 | 15 | yx | 1 | 0 |  |  | {"en":"In7Status"}
1016 | in8Status | IN8状态 | 1 | 16 | yx | 1 | 0 |  |  | {"en":"In8Status"}
1017 | in9Status | IN9状态 | 1 | 17 | yx | 1 | 0 |  |  | {"en":"In9Status"}
1018 | in10Status | IN10状态 | 1 | 18 | yx | 1 | 0 |  |  | {"en":"In10Status"}
1019 | in11Status | IN11状态 | 1 | 19 | yx | 1 | 0 |  |  | {"en":"In11Status"}
1020 | mainBreakerStatus | 主断路器分合闸状态 | 1 | 20 | yx | 1 | 0 |  |  | {"en":"MainBreakerStatus"}
2000 | remoteLocalMode | 远程就地控制模式 | 1 | 0 | yt_short | 1 | 0 |  |  | {"en":"RemoteLocalMode"} | 0 就地模式¦Local mode 1 远程模式¦Remote mode
2001 | maxOutputPowerLimit | 最大输出功率限制 | 1 | 1 | yt_short | 0.1 | 0 | kW |  | {"en":"MaxOutputPowerLimit"}
2002 | operationMode | 运行模式选择 | 1 | 2 | yt_short | 1 | 0 |  |  | {"en":"OperationMode"} | 0 无¦None 1 恒流¦Constant current 2 恒压¦Constant voltage 3 恒功率¦Constant power 4 直流恒压¦DC constant voltage
2003 | gridReactiveRegMode | 并网无功调节方式 | 1 | 3 | yt_short | 1 | 0 |  |  | {"en":"GridReactiveRegMode"} | 0 无功功率¦Reactive power 1 功率因数¦Power factor
2004 | activeReactivePriority | 有功/无功优先使能 | 1 | 4 | yt_short | 1 | 0 |  |  | {"en":"ActiveReactivePriority"} | 0 按比例分配¦Proportional distribution 1 有功优先¦Active power priority 2 无功优先¦Reactive power priority
2005 | gridActivePowerSet | 并网有功给定 | 1 | 5 | yt_short | 0.1 | 0 | kW |  | {"en":"GridActivePowerSet"}
2006 | gridReactivePowerSet | 并网无功给定 | 1 | 6 | yt_short | 0.1 | 0 | kVar |  | {"en":"GridReactivePowerSet"}
2007 | gridPowerFactorSet | 并网功率因数给定 | 1 | 7 | yt_short | 0.001 | 0 |  |  | {"en":"GridPowerFactorSet"}
2008 | vfVoltageSet | VF电压给定 | 1 | 8 | yt_short | 0.1 | 0 | V |  | {"en":"VfVoltageSet"}
2009 | vfFrequencySet | VF频率给定 | 1 | 9 | yt_short | 0.01 | 0 | Hz |  | {"en":"VfFrequencySet"}
2010 | gridConstantCurrent | 并网恒流电流 | 1 | 10 | yt_short | 0.1 | 0 | A |  | {"en":"GridConstantCurrent"}
2011 | gridConstantVoltage | 并网恒压电压值 | 1 | 11 | yt_short | 0.1 | 0 | V |  | {"en":"GridConstantVoltage"}
2012 | vsgVoltageSet | VSG电压给定 | 1 | 12 | yt_short | 0.1 | 0 | V |  | {"en":"VsgVoltageSet"}
2013 | vsgFrequencySet | VSG频率给定 | 1 | 13 | yt_short | 0.1 | 0 | Hz |  | {"en":"VsgFrequencySet"}
2014 | vsgSecondaryActivePowerSet | VSG二次有功给定 | 1 | 14 | yt_short | 0.1 | 0 | kW |  | {"en":"VsgSecondaryActivePowerSet"}
2015 | vsgSecondaryReactivePowerSet | VSG二次无功给定 | 1 | 15 | yt_short | 0.1 | 0 | kVar |  | {"en":"VsgSecondaryReactivePowerSet"}
2016 | dcAllowChargeVoltage | 储能直流允许充电电压 | 1 | 16 | yt_short | 0.01 | 0 | V |  | {"en":"DcAllowChargeVoltage"}
2017 | dcAllowDischargeVoltage | 储能直流允许放电电压 | 1 | 17 | yt_short | 0.1 | 0 | V |  | {"en":"DcAllowDischargeVoltage"}
2018 | dcAllowChargeCurrent | 储能直流允许充电电流 | 1 | 18 | yt_short | 0.1 | 0 | A |  | {"en":"DcAllowChargeCurrent"}
2019 | dcAllowDischargeCurrent | 储能直流允许放电电流 | 1 | 19 | yt_short | 0.1 | 0 | A |  | {"en":"DcAllowDischargeCurrent"}
2020 | pcsStartStopCtrl | 单台PCS启停控制 | 1 | 20 | yt_short | 1 | 0 |  |  | {"en":"PcsStartStopCtrl"} |  |  |  | BIT0:PCS1 BIT1:PCS2 … BIT15:PCS16
2021 | standbyEnable | 待机使能 | 1 | 21 | yt_short | 1 | 0 |  |  | {"en":"StandbyEnable"} | 0 禁止自动待机¦Auto standby disabled 1 允许自动待机¦Auto standby enabled
2022 | socBalanceCtrl | SOC均衡控制 | 1 | 22 | yt_short | 1 | 0 |  |  | {"en":"SocBalanceCtrl"} |  |  |  | Bit0: 均衡算法禁用 Bit1: 均衡死区使能 Bit2: 涓流控制使能 Bit3: SOH均衡使能 Bit4: 效率优化使能
2023 | powerRegDeadZone | 功率调节死区 | 1 | 23 | yt_short | 1 | 0 | kW |  | {"en":"PowerRegDeadZone"}
2024 | powerRegPeriod | 功率调节周期 | 1 | 24 | yt_short | 0.1 | 0 | ms |  | {"en":"PowerRegPeriod"}
2025 | powerRampCoeff | 功率调节速率/功率爬坡系数 | 1 | 25 | yt_short | 1 | 0 | kW/s |  | {"en":"PowerRampCoeff"}
2026 | socBalanceDeadZone | SOC均衡死区 | 1 | 26 | yt_short | 0.1 | 0 | % |  | {"en":"SocBalanceDeadZone"}
2027 | chargeTrickleThreshold | 充电涓流阈值 | 1 | 27 | yt_short | 0.1 | 0 | % |  | {"en":"ChargeTrickleThreshold"}
2028 | dischargeTrickleThreshold | 放电涓流阈值 | 1 | 28 | yt_short | 0.1 | 0 | % |  | {"en":"DischargeTrickleThreshold"}
2029 | sysTimeSec | 系统时间（秒） | 1 | 29 | yt_short | 0.1 | 0 |  |  | {"en":"SysTimeSec"}
2030 | sysTimeMin | 系统时间（分） | 1 | 30 | yt_short | 1 | 0 |  |  | {"en":"SysTimeMin"}
2031 | sysTimeHour | 系统时间（时） | 1 | 31 | yt_short | 1 | 0 |  |  | {"en":"SysTimeHour"}
2032 | sysTimeDay | 系统时间（日） | 1 | 32 | yt_short | 1 | 0 |  |  | {"en":"SysTimeDay"}
2033 | sysTimeMonth | 系统时间（月） | 1 | 33 | yt_short | 1 | 0 |  |  | {"en":"SysTimeMonth"}
2034 | sysTimeYear | 系统时间（年） | 1 | 34 | yt_short | 1 | 0 |  |  | {"en":"SysTimeYear"}
2035 | timeSyncCmd | 一键对时指令 | 1 | 35 | yt_short | 1 | 0 |  |  | {"en":"TimeSyncCmd"} | 0 无指令¦No command 1 一键对时¦One-key time synchronization
2036 | alarmTripEnable | 报警输出是否跳闸 | 1 | 36 | yt_short | 1 | 0 |  |  | {"en":"AlarmTripEnable"} | 0 只输出报警¦Alarm output only 1 报警同时跳闸¦Alarm output with trip
2037 | armReset | ARM复位 | 1 | 37 | yt_short | 1 | 0 |  |  | {"en":"ArmReset"}
2038 | sccFactoryReset | 子站控制器恢复出厂设置 | 1 | 38 | yt_short | 1 | 0 |  |  | {"en":"SccFactoryReset"} | 0 无效¦Invalid 1 恢复默认设置¦Restore default settings
2039 | minHighEffLoadRate | 最低高效负载率 | 1 | 39 | yt_short | 0.1 | 0 | % |  | {"en":"MinHighEffLoadRate"}
2040 | stateSwitchBlockTime | 状态切换防震荡闭锁时间 | 1 | 40 | yt_short | 1 | 0 | S |  | {"en":"StateSwitchBlockTime"}
3000 | remoteStartCmd | 远程启动指令 | 1 | 0 | yk | 1 | 0 |  |  | {"en":"RemoteStartCmd"} | 0 停机¦Stop 1 启动¦Start
3001 | remoteReset | 远程复位 | 1 | 1 | yk | 1 | 0 |  |  | {"en":"RemoteReset"} | 1 有效¦Valid 0 无效¦Invalid
3002 | remoteEStop | 远程急停 | 1 | 2 | yk | 1 | 0 |  |  | {"en":"RemoteEStop"} | 1 有效¦Valid 0 无效¦Invalid
3003 | remoteRestart | 远程重启 | 1 | 3 | yk | 1 | 0 |  |  | {"en":"RemoteRestart"} | 1 有效¦Valid 0 无效¦Invalid
3004 | gridOffGridMode | 并离网模式 | 1 | 4 | yk | 1 | 0 |  |  | {"en":"GridOffGridMode"} | 0 并网¦Grid-connected 1 离网¦Off-grid
3005 | mainBreakerCtrl | 主断路器分合闸控制 | 1 | 5 | yk | 1 | 0 |  |  | {"en":"MainBreakerCtrl"} | 0 分闸¦Open 1 合闸¦Closed
1002 | groundSwitch | 接地刀闸 | 1 | 2 | yx |  |  |  | 1 | {"en":"Ground Switch"} | 0 分闸¦Open 1 合闸¦Closed
1003 | protectTrip | 保护动作 | 1 | 3 | yx |  |  |  | 1 | {"en":"Protection Trip"} |  |  | 3
2001 | voltageA | A相电压 | 1 | 16385 | yc | 0.1 | 0 | V | 1 | {"en":"Voltage A"}
2002 | currentA | A相电流 | 1 | 16386 | yc | 0.01 | 0 | A | 1 | {"en":"Current A"}
2003 | activePower | 有功功率 | 1 | 16387 | yc | 0.001 | 0 | kW | 1 | {"en":"Active Power"}
2004 | temperature | 温度 | 1 | 16388 | yc | 0.1 | -40 | ℃ | 1 | {"en":"Temperature"}
2005 | frequency | 频率 | 1 | 16389 | yc | 1 | 0 | Hz | 1 | {"en":"Frequency"}
2006 | faultWord | 故障字 | 1 | 16390 | yc | 1 | 0 |  | 1 | {"en":"Fault Word"} |  | 保护动作¦Protection Trip¦3 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0 备用¦Spare¦0
3001 | breakerCmd | 断路器遥控 | 1 | 24577 | yk |  |  |  | 1
3002 | switchCmd | 刀闸遥控(双点) | 1 | 24578 | yk_double |  |  |  | 1
4001 | powerSetpoint | 有功功率设定 | 1 | 25089 | yt_short | 1 | 0 | kW | 1
4002 | voltageSetpoint | 电压设定 | 1 | 25090 | yt_scaled | 0.1 | 0 | V | 1
4003 | tapChange | 分接头调节 | 1 | 25091 | yt_step |  |  |  | 1
9001 | spare | 备用点 | 1 | 99 | yx |  |  |  | 0