## iec61850
id | key | name | ref | fc | type | scale | offset | unit | enable | trans | status_words | warn_bits | level | ctl_opts | feedback
1001 | staGGIO1_Ind1 | 工作状态-停机 | MONT/staGGIO1.Ind1.stVal | ST | yx |  |  |  | 1
1002 | staGGIO1_Ind2 | 工作状态-待机 | MONT/staGGIO1.Ind2.stVal | ST | yx |  |  |  | 1
1003 | staGGIO1_Ind3 | 工作状态-充电运行 | MONT/staGGIO1.Ind3.stVal | ST | yx |  |  |  | 1
1004 | staGGIO1_Ind4 | 工作状态-放电运行 | MONT/staGGIO1.Ind4.stVal | ST | yx |  |  |  | 1
1005 | staGGIO1_Ind5 | 工作状态-故障 | MONT/staGGIO1.Ind5.stVal | ST | yx |  |  |  | 1
1006 | staGGIO1_Ind6 | 工作状态-零功率 | MONT/staGGIO1.Ind6.stVal | ST | yx |  |  |  | 1
1007 | staGGIO1_Ind7 | 工作状态-告警 | MONT/staGGIO1.Ind7.stVal | ST | yx |  |  |  | 1
1008 | staGGIO1_Ind8 | PCS并离网状态 | MONT/staGGIO1.Ind8.stVal | ST | yx |  |  |  | 1
1009 | staGGIO1_Ind9 | IN0告警 | MONT/staGGIO1.Ind9.stVal | ST | yx |  |  |  | 1
1010 | staGGIO1_Ind10 | IN1告警 | MONT/staGGIO1.Ind10.stVal | ST | yx |  |  |  | 1
1011 | staGGIO1_Ind11 | IN2告警 | MONT/staGGIO1.Ind11.stVal | ST | yx |  |  |  | 1
1012 | staGGIO1_Ind12 | IN3告警 | MONT/staGGIO1.Ind12.stVal | ST | yx |  |  |  | 1
1013 | staGGIO1_Ind13 | IN4告警 | MONT/staGGIO1.Ind13.stVal | ST | yx |  |  |  | 1
1014 | staGGIO1_Ind14 | IN5告警 | MONT/staGGIO1.Ind14.stVal | ST | yx |  |  |  | 1
1015 | staGGIO1_Ind15 | IN6告警 | MONT/staGGIO1.Ind15.stVal | ST | yx |  |  |  | 1
1016 | staGGIO1_Ind16 | IN7告警 | MONT/staGGIO1.Ind16.stVal | ST | yx |  |  |  | 1
1017 | staGGIO2_Ind1 | IN8告警 | MONT/staGGIO2.Ind1.stVal | ST | yx |  |  |  | 1
1018 | staGGIO2_Ind2 | IN9告警 | MONT/staGGIO2.Ind2.stVal | ST | yx |  |  |  | 1
1019 | staGGIO2_Ind3 | IN10告警 | MONT/staGGIO2.Ind3.stVal | ST | yx |  |  |  | 1
1020 | staGGIO2_Ind4 | IN11告警 | MONT/staGGIO2.Ind4.stVal | ST | yx |  |  |  | 1
1021 | staGGIO2_Ind5 | 通信告警 | MONT/staGGIO2.Ind5.stVal | ST | yx |  |  |  | 1
1022 | staGGIO2_Ind6 | 主断路器分合闸状态 | MONT/staGGIO2.Ind6.stVal | ST | yx |  |  |  | 1
1023 | ctlGAPC1_SPCSO1 | 远程启停控制-回读 | MONT/ctlGAPC1.SPCSO1.stVal | ST | yx |  |  |  | 1
1024 | ctlGAPC1_SPCSO2 | 远程复位-回读 | MONT/ctlGAPC1.SPCSO2.stVal | ST | yx |  |  |  | 1
1025 | ctlGAPC1_SPCSO3 | 远程急停-回读 | MONT/ctlGAPC1.SPCSO3.stVal | ST | yx |  |  |  | 1
1026 | ctlGAPC1_SPCSO4 | 远程重启-回读 | MONT/ctlGAPC1.SPCSO4.stVal | ST | yx |  |  |  | 1
1027 | ctlGAPC1_SPCSO5 | 并离网模式切换-回读 | MONT/ctlGAPC1.SPCSO5.stVal | ST | yx |  |  |  | 1
1028 | ctlGAPC1_SPCSO6 | 主断路器分合闸控制-回读 | MONT/ctlGAPC1.SPCSO6.stVal | ST | yx |  |  |  | 1
2001 | MMXU1_Hz | 电网频率 | MONT/MMXU1.Hz.mag.f | MX | yc |  |  |  | 1
2002 | MMXU1_PPV_phsAB | 线电压-phsAB | MONT/MMXU1.PPV.phsAB.cVal.mag.f | MX | yc |  |  |  | 1
2003 | MMXU1_PPV_phsBC | 线电压-phsBC | MONT/MMXU1.PPV.phsBC.cVal.mag.f | MX | yc |  |  |  | 1
2004 | MMXU1_PPV_phsCA | 线电压-phsCA | MONT/MMXU1.PPV.phsCA.cVal.mag.f | MX | yc |  |  |  | 1
2005 | MMXU1_A_phsA | 相电流-phsA | MONT/MMXU1.A.phsA.cVal.mag.f | MX | yc |  |  |  | 1
2006 | MMXU1_A_phsB | 相电流-phsB | MONT/MMXU1.A.phsB.cVal.mag.f | MX | yc |  |  |  | 1
2007 | MMXU1_A_phsC | 相电流-phsC | MONT/MMXU1.A.phsC.cVal.mag.f | MX | yc |  |  |  | 1
2008 | dcMMXN1_Vol | 直流电压典型值 | MONT/dcMMXN1.Vol.mag.f | MX | yc |  |  |  | 1
2009 | dcMMXN1_Amp | 直流总电流 | MONT/dcMMXN1.Amp.mag.f | MX | yc |  |  |  | 1
2010 | dcMMXN1_Watt | 直流总功率 | MONT/dcMMXN1.Watt.mag.f | MX | yc |  |  |  | 1
2011 | MMXU1_TotPF | 总功率因数 | MONT/MMXU1.TotPF.mag.f | MX | yc |  |  |  | 1
2012 | MMXU1_TotVA | 总视在功率 | MONT/MMXU1.TotVA.mag.f | MX | yc |  |  |  | 1
2013 | MMXU1_TotW | PCS实时有功功率 | MONT/MMXU1.TotW.mag.f | MX | yc |  |  |  | 1
2014 | MMXU1_TotVAr | PCS实时无功功率 | MONT/MMXU1.TotVAr.mag.f | MX | yc |  |  |  | 1
2015 | kwGGIO1_AnIn1 | 累计日充电量 | MONT/kwGGIO1.AnIn1.mag.f | MX | yc |  |  |  | 1
2016 | kwGGIO1_AnIn2 | 累计日放电量 | MONT/kwGGIO1.AnIn2.mag.f | MX | yc |  |  |  | 1
2017 | kwGGIO1_AnIn3 | 系统累计充电量 | MONT/kwGGIO1.AnIn3.mag.f | MX | yc |  |  |  | 1
2018 | kwGGIO1_AnIn4 | 系统累计放电量 | MONT/kwGGIO1.AnIn4.mag.f | MX | yc |  |  |  | 1
2019 | devGGIO1_AnIn1 | PCS最大可充有功功率 | MONT/devGGIO1.AnIn1.mag.f | MX | yc |  |  |  | 1
2020 | devGGIO1_AnIn2 | PCS最大可放有功功率 | MONT/devGGIO1.AnIn2.mag.f | MX | yc |  |  |  | 1
2021 | devGGIO1_AnIn3 | PCS最大可用容性无功功率 | MONT/devGGIO1.AnIn3.mag.f | MX | yc |  |  |  | 1
2022 | devGGIO1_AnIn4 | PCS最大可用感性无功功率 | MONT/devGGIO1.AnIn4.mag.f | MX | yc |  |  |  | 1
2023 | devGGIO1_AnIn5 | SOC | MONT/devGGIO1.AnIn5.mag.f | MX | yc |  |  |  | 1
2024 | devGGIO1_AnIn6 | SOH | MONT/devGGIO1.AnIn6.mag.f | MX | yc |  |  |  | 1
2025 | devGGIO1_AnIn7 | 电网电压不平衡度 | MONT/devGGIO1.AnIn7.mag.f | MX | yc |  |  |  | 1
2026 | devGGIO1_AnIn8 | 输出电压不平衡度 | MONT/devGGIO1.AnIn8.mag.f | MX | yc |  |  |  | 1
2027 | devGGIO1_AnIn9 | 输出电流不平衡度 | MONT/devGGIO1.AnIn9.mag.f | MX | yc |  |  |  | 1
2028 | devGGIO1_AnIn10 | PCS IGBT最大温度站点 | MONT/devGGIO1.AnIn10.mag.f | MX | yc |  |  |  | 1
2029 | devGGIO1_AnIn11 | PCS IGBT最大温度 | MONT/devGGIO1.AnIn11.mag.f | MX | yc |  |  |  | 1
2030 | devGGIO1_AnIn12 | PCS IGBT最小温度站点 | MONT/devGGIO1.AnIn12.mag.f | MX | yc |  |  |  | 1
2031 | devGGIO1_AnIn13 | PCS IGBT最小温度 | MONT/devGGIO1.AnIn13.mag.f | MX | yc |  |  |  | 1
2032 | devGGIO1_AnIn14 | PCS 环境最大温度站点 | MONT/devGGIO1.AnIn14.mag.f | MX | yc |  |  |  | 1
2033 | devGGIO1_AnIn15 | PCS 环境最大温度 | MONT/devGGIO1.AnIn15.mag.f | MX | yc |  |  |  | 1
2034 | devGGIO1_AnIn16 | PCS 环境最小温度站点 | MONT/devGGIO1.AnIn16.mag.f | MX | yc |  |  |  | 1
2035 | devGGIO1_AnIn17 | PCS 环境最小温度 | MONT/devGGIO1.AnIn17.mag.f | MX | yc |  |  |  | 1
2036 | devGGIO1_AnIn18 | 环境湿度 | MONT/devGGIO1.AnIn18.mag.f | MX | yc |  |  |  | 1
2037 | devGGIO1_AnIn19 | 系统正极绝缘电阻最小值站点 | MONT/devGGIO1.AnIn19.mag.f | MX | yc |  |  |  | 1
2038 | devGGIO1_AnIn20 | 系统正极绝缘电阻最小值 | MONT/devGGIO1.AnIn20.mag.f | MX | yc |  |  |  | 1
2039 | devGGIO2_AnIn1 | 系统负极绝缘电阻最小值站点 | MONT/devGGIO2.AnIn1.mag.f | MX | yc |  |  |  | 1
2040 | devGGIO2_AnIn2 | 系统负极绝缘电阻最小值 | MONT/devGGIO2.AnIn2.mag.f | MX | yc |  |  |  | 1
2041 | devGGIO2_AnIn3 | 功率调节死区[devGGIO2.AnIn3] | MONT/devGGIO2.AnIn3.mag.f | MX | yc |  |  |  | 1
2042 | devGGIO2_AnIn4 | SOC均衡死区[devGGIO2.AnIn4] | MONT/devGGIO2.AnIn4.mag.f | MX | yc |  |  |  | 1
2043 | devGGIO2_AnIn5 | 功率调节周期[devGGIO2.AnIn5] | MONT/devGGIO2.AnIn5.mag.f | MX | yc |  |  |  | 1
2044 | devGGIO2_AnIn6 | 功率调节速率 | MONT/devGGIO2.AnIn6.mag.f | MX | yc |  |  |  | 1
2045 | devGGIO2_AnIn7 | 充电涓流阈值[devGGIO2.AnIn7] | MONT/devGGIO2.AnIn7.mag.f | MX | yc |  |  |  | 1
2046 | devGGIO2_AnIn8 | 放电涓流阈值[devGGIO2.AnIn8] | MONT/devGGIO2.AnIn8.mag.f | MX | yc |  |  |  | 1
2047 | devGGIO2_AnIn9 | 系统时间（秒）[devGGIO2.AnIn9] | MONT/devGGIO2.AnIn9.mag.f | MX | yc |  |  |  | 1
2048 | devGGIO2_AnIn10 | 系统时间（分）[devGGIO2.AnIn10] | MONT/devGGIO2.AnIn10.mag.f | MX | yc |  |  |  | 1
2049 | devGGIO2_AnIn11 | 系统时间（时）[devGGIO2.AnIn11] | MONT/devGGIO2.AnIn11.mag.f | MX | yc |  |  |  | 1
2050 | devGGIO2_AnIn12 | 系统时间（日）[devGGIO2.AnIn12] | MONT/devGGIO2.AnIn12.mag.f | MX | yc |  |  |  | 1
2051 | devGGIO2_AnIn13 | 系统时间（月）[devGGIO2.AnIn13] | MONT/devGGIO2.AnIn13.mag.f | MX | yc |  |  |  | 1
2052 | devGGIO2_AnIn14 | 系统时间（年）[devGGIO2.AnIn14] | MONT/devGGIO2.AnIn14.mag.f | MX | yc |  |  |  | 1
2053 | devGGIO2_AnIn15 | 子站控制器告警 | MONT/devGGIO2.AnIn15.mag.f | MX | yc |  |  |  | 1
2054 | devGGIO2_AnIn16 | ECAT事件告警 | MONT/devGGIO2.AnIn16.mag.f | MX | yc |  |  |  | 1
2055 | devGGIO2_AnIn17 | TCP事件告警 | MONT/devGGIO2.AnIn17.mag.f | MX | yc |  |  |  | 1
2056 | devGGIO2_AnIn18 | RTU事件告警 | MONT/devGGIO2.AnIn18.mag.f | MX | yc |  |  |  | 1
2057 | devGGIO2_AnIn19 | EMU-IO状态1 | MONT/devGGIO2.AnIn19.mag.f | MX | yc |  |  |  | 1
2058 | devGGIO2_AnIn20 | EMU-IO状态2 | MONT/devGGIO2.AnIn20.mag.f | MX | yc |  |  |  | 1
2059 | devGGIO3_AnIn1 | PCS1故障码 | MONT/devGGIO3.AnIn1.mag.f | MX | yc |  |  |  | 1
2060 | devGGIO3_AnIn2 | PCS2故障码 | MONT/devGGIO3.AnIn2.mag.f | MX | yc |  |  |  | 1
2061 | devGGIO3_AnIn3 | PCS3故障码 | MONT/devGGIO3.AnIn3.mag.f | MX | yc |  |  |  | 1
2062 | devGGIO3_AnIn4 | PCS4故障码 | MONT/devGGIO3.AnIn4.mag.f | MX | yc |  |  |  | 1
2063 | devGGIO3_AnIn5 | PCS5故障码 | MONT/devGGIO3.AnIn5.mag.f | MX | yc |  |  |  | 1
2064 | devGGIO3_AnIn6 | PCS6故障码 | MONT/devGGIO3.AnIn6.mag.f | MX | yc |  |  |  | 1
2065 | devGGIO3_AnIn7 | PCS7故障码 | MONT/devGGIO3.AnIn7.mag.f | MX | yc |  |  |  | 1
2066 | devGGIO3_AnIn8 | PCS8故障码 | MONT/devGGIO3.AnIn8.mag.f | MX | yc |  |  |  | 1
2067 | devGGIO3_AnIn9 | PCS9故障码 | MONT/devGGIO3.AnIn9.mag.f | MX | yc |  |  |  | 1
2068 | devGGIO3_AnIn10 | PCS10故障码 | MONT/devGGIO3.AnIn10.mag.f | MX | yc |  |  |  | 1
2069 | devGGIO3_AnIn11 | PCS11故障码 | MONT/devGGIO3.AnIn11.mag.f | MX | yc |  |  |  | 1
2070 | devGGIO3_AnIn12 | PCS12故障码 | MONT/devGGIO3.AnIn12.mag.f | MX | yc |  |  |  | 1
2071 | devGGIO3_AnIn13 | 液冷机组故障 | MONT/devGGIO3.AnIn13.mag.f | MX | yc |  |  |  | 1
2072 | devGGIO3_AnIn14 | SCC DI故障 | MONT/devGGIO3.AnIn14.mag.f | MX | yc |  |  |  | 1
2073 | devGGIO3_AnIn15 | SCC 配置故障 | MONT/devGGIO3.AnIn15.mag.f | MX | yc |  |  |  | 1
2074 | devGGIO4_AnIn1 | 变电所.额定功率 | MONT/devGGIO4.AnIn1.mag.f | MX | yc |  |  |  | 1
2075 | devGGIO4_AnIn2 | 变电所.综合工作状态 | MONT/devGGIO4.AnIn2.mag.f | MX | yc |  |  |  | 1
2076 | setGAPC1_StrVal1 | 远程就地控制模式-回读 | MONT/setGAPC1.StrVal1.mxVal.f | MX | yc |  |  |  | 1
2077 | setGAPC1_StrVal2 | 最大输出功率限制-回读 | MONT/setGAPC1.StrVal2.mxVal.f | MX | yc |  |  |  | 1
2078 | setGAPC1_StrVal3 | 运行模式选择-回读 | MONT/setGAPC1.StrVal3.mxVal.f | MX | yc |  |  |  | 1
2079 | setGAPC1_StrVal4 | 并网无功调节方式-回读 | MONT/setGAPC1.StrVal4.mxVal.f | MX | yc |  |  |  | 1
2080 | setGAPC1_StrVal5 | 有功/无功优先使能-回读 | MONT/setGAPC1.StrVal5.mxVal.f | MX | yc |  |  |  | 1
2081 | setGAPC1_StrVal6 | 并网有功给定-回读 | MONT/setGAPC1.StrVal6.mxVal.f | MX | yc |  |  |  | 1
2082 | setGAPC1_StrVal7 | 并网无功给定-回读 | MONT/setGAPC1.StrVal7.mxVal.f | MX | yc |  |  |  | 1
2083 | setGAPC1_StrVal8 | 并网功率因数给定-回读 | MONT/setGAPC1.StrVal8.mxVal.f | MX | yc |  |  |  | 1
2084 | setGAPC1_StrVal9 | VF电压给定-回读 | MONT/setGAPC1.StrVal9.mxVal.f | MX | yc |  |  |  | 1
2085 | setGAPC1_StrVal10 | VF频率给定-回读 | MONT/setGAPC1.StrVal10.mxVal.f | MX | yc |  |  |  | 1
2086 | setGAPC1_StrVal11 | 并网恒流电流-回读 | MONT/setGAPC1.StrVal11.mxVal.f | MX | yc |  |  |  | 1
2087 | setGAPC1_StrVal12 | 并网恒压电压值-回读 | MONT/setGAPC1.StrVal12.mxVal.f | MX | yc |  |  |  | 1
2088 | setGAPC1_StrVal13 | VSG电压给定-回读 | MONT/setGAPC1.StrVal13.mxVal.f | MX | yc |  |  |  | 1
2089 | setGAPC1_StrVal14 | VSG频率给定-回读 | MONT/setGAPC1.StrVal14.mxVal.f | MX | yc |  |  |  | 1
2090 | setGAPC1_StrVal15 | VSG二次有功给定-回读 | MONT/setGAPC1.StrVal15.mxVal.f | MX | yc |  |  |  | 1
2091 | setGAPC1_StrVal16 | VSG二次无功给定-回读 | MONT/setGAPC1.StrVal16.mxVal.f | MX | yc |  |  |  | 1
2092 | setGAPC2_StrVal1 | 储能直流允许充电电压-回读 | MONT/setGAPC2.StrVal1.mxVal.f | MX | yc |  |  |  | 1
2093 | setGAPC2_StrVal2 | 储能直流允许放电电压-回读 | MONT/setGAPC2.StrVal2.mxVal.f | MX | yc |  |  |  | 1
2094 | setGAPC2_StrVal3 | 储能直流允许充电电流-回读 | MONT/setGAPC2.StrVal3.mxVal.f | MX | yc |  |  |  | 1
2095 | setGAPC2_StrVal4 | 储能直流允许放电电流-回读 | MONT/setGAPC2.StrVal4.mxVal.f | MX | yc |  |  |  | 1
2096 | setGAPC2_StrVal5 | 单台PCS启停控制-回读 | MONT/setGAPC2.StrVal5.mxVal.f | MX | yc |  |  |  | 1
2097 | setGAPC2_StrVal6 | 待机使能-回读 | MONT/setGAPC2.StrVal6.mxVal.f | MX | yc |  |  |  | 1
2098 | setGAPC2_StrVal7 | SOC均衡控制-回读 | MONT/setGAPC2.StrVal7.mxVal.f | MX | yc |  |  |  | 1
2099 | setGAPC2_StrVal8 | 功率调节死区-回读 | MONT/setGAPC2.StrVal8.mxVal.f | MX | yc |  |  |  | 1
2100 | setGAPC2_StrVal9 | 功率调节周期-回读 | MONT/setGAPC2.StrVal9.mxVal.f | MX | yc |  |  |  | 1
2101 | setGAPC2_StrVal10 | 功率调节速率/功率爬坡系数-回读 | MONT/setGAPC2.StrVal10.mxVal.f | MX | yc |  |  |  | 1
2102 | setGAPC2_StrVal11 | SOC均衡死区-回读 | MONT/setGAPC2.StrVal11.mxVal.f | MX | yc |  |  |  | 1
2103 | setGAPC2_StrVal12 | 充电涓流阈值-回读 | MONT/setGAPC2.StrVal12.mxVal.f | MX | yc |  |  |  | 1
2104 | setGAPC2_StrVal13 | 放电涓流阈值-回读 | MONT/setGAPC2.StrVal13.mxVal.f | MX | yc |  |  |  | 1
2105 | setGAPC2_StrVal14 | 系统时间（秒）-回读 | MONT/setGAPC2.StrVal14.mxVal.f | MX | yc |  |  |  | 1
2106 | setGAPC2_StrVal15 | 系统时间（分）-回读 | MONT/setGAPC2.StrVal15.mxVal.f | MX | yc |  |  |  | 1
2107 | setGAPC2_StrVal16 | 系统时间（时）-回读 | MONT/setGAPC2.StrVal16.mxVal.f | MX | yc |  |  |  | 1
2108 | setGAPC3_StrVal1 | 系统时间（日）-回读 | MONT/setGAPC3.StrVal1.mxVal.f | MX | yc |  |  |  | 1
2109 | setGAPC3_StrVal2 | 系统时间（月）-回读 | MONT/setGAPC3.StrVal2.mxVal.f | MX | yc |  |  |  | 1
2110 | setGAPC3_StrVal3 | 系统时间（年）-回读 | MONT/setGAPC3.StrVal3.mxVal.f | MX | yc |  |  |  | 1
2111 | setGAPC3_StrVal4 | 一键对时指令-回读 | MONT/setGAPC3.StrVal4.mxVal.f | MX | yc |  |  |  | 1
2112 | setGAPC3_StrVal5 | 报警输出是否跳闸-回读 | MONT/setGAPC3.StrVal5.mxVal.f | MX | yc |  |  |  | 1
2113 | setGAPC3_StrVal6 | PCS ARM复位-回读 | MONT/setGAPC3.StrVal6.mxVal.f | MX | yc |  |  |  | 1
2114 | setGAPC3_StrVal7 | 子站控制器恢复出厂设置-回读 | MONT/setGAPC3.StrVal7.mxVal.f | MX | yc |  |  |  | 1
2115 | setGAPC3_StrVal8 | 最低高效负载率-回读 | MONT/setGAPC3.StrVal8.mxVal.f | MX | yc |  |  |  | 1
2116 | setGAPC3_StrVal9 | 状态切换防震荡闭锁时间-回读 | MONT/setGAPC3.StrVal9.mxVal.f | MX | yc |  |  |  | 1
3001 | ctlGAPC1_SPCSO1_cmd | 远程启停控制 | MONT/ctlGAPC1.SPCSO1 |  | yk |  |  |  | 1 | [5 empty] | ctlGAPC1_SPCSO1
3002 | ctlGAPC1_SPCSO2_cmd | 远程复位 | MONT/ctlGAPC1.SPCSO2 |  | yk |  |  |  | 0 | [5 empty] | ctlGAPC1_SPCSO2
3003 | ctlGAPC1_SPCSO3_cmd | 远程急停 | MONT/ctlGAPC1.SPCSO3 |  | yk |  |  |  | 0 | [5 empty] | ctlGAPC1_SPCSO3
3004 | ctlGAPC1_SPCSO4_cmd | 远程重启 | MONT/ctlGAPC1.SPCSO4 |  | yk |  |  |  | 0 | [5 empty] | ctlGAPC1_SPCSO4
3005 | ctlGAPC1_SPCSO5_cmd | 并离网模式切换 | MONT/ctlGAPC1.SPCSO5 |  | yk |  |  |  | 1 | [5 empty] | ctlGAPC1_SPCSO5
3006 | ctlGAPC1_SPCSO6_cmd | 主断路器分合闸控制 | MONT/ctlGAPC1.SPCSO6 |  | yk |  |  |  | 1 | [5 empty] | ctlGAPC1_SPCSO6
4001 | setGAPC1_StrVal1_cmd | 远程就地控制模式 | MONT/setGAPC1.StrVal1 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal1
4002 | setGAPC1_StrVal2_cmd | 最大输出功率限制 | MONT/setGAPC1.StrVal2 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal2
4003 | setGAPC1_StrVal3_cmd | 运行模式选择 | MONT/setGAPC1.StrVal3 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal3
4004 | setGAPC1_StrVal4_cmd | 并网无功调节方式 | MONT/setGAPC1.StrVal4 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal4
4005 | setGAPC1_StrVal5_cmd | 有功/无功优先使能 | MONT/setGAPC1.StrVal5 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal5
4006 | setGAPC1_StrVal6_cmd | 并网有功给定 | MONT/setGAPC1.StrVal6 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal6
4007 | setGAPC1_StrVal7_cmd | 并网无功给定 | MONT/setGAPC1.StrVal7 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal7
4008 | setGAPC1_StrVal8_cmd | 并网功率因数给定 | MONT/setGAPC1.StrVal8 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal8
4009 | setGAPC1_StrVal9_cmd | VF电压给定 | MONT/setGAPC1.StrVal9 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal9
4010 | setGAPC1_StrVal10_cmd | VF频率给定 | MONT/setGAPC1.StrVal10 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal10
4011 | setGAPC1_StrVal11_cmd | 并网恒流电流 | MONT/setGAPC1.StrVal11 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal11
4012 | setGAPC1_StrVal12_cmd | 并网恒压电压值 | MONT/setGAPC1.StrVal12 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal12
4013 | setGAPC1_StrVal13_cmd | VSG电压给定 | MONT/setGAPC1.StrVal13 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal13
4014 | setGAPC1_StrVal14_cmd | VSG频率给定 | MONT/setGAPC1.StrVal14 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal14
4015 | setGAPC1_StrVal15_cmd | VSG二次有功给定 | MONT/setGAPC1.StrVal15 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal15
4016 | setGAPC1_StrVal16_cmd | VSG二次无功给定 | MONT/setGAPC1.StrVal16 |  | yt |  |  |  | 1 | [5 empty] | setGAPC1_StrVal16
4017 | setGAPC2_StrVal1_cmd | 储能直流允许充电电压 | MONT/setGAPC2.StrVal1 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal1
4018 | setGAPC2_StrVal2_cmd | 储能直流允许放电电压 | MONT/setGAPC2.StrVal2 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal2
4019 | setGAPC2_StrVal3_cmd | 储能直流允许充电电流 | MONT/setGAPC2.StrVal3 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal3
4020 | setGAPC2_StrVal4_cmd | 储能直流允许放电电流 | MONT/setGAPC2.StrVal4 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal4
4021 | setGAPC2_StrVal5_cmd | 单台PCS启停控制 | MONT/setGAPC2.StrVal5 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal5
4022 | setGAPC2_StrVal6_cmd | 待机使能 | MONT/setGAPC2.StrVal6 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal6
4023 | setGAPC2_StrVal7_cmd | SOC均衡控制 | MONT/setGAPC2.StrVal7 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal7
4024 | setGAPC2_StrVal8_cmd | 功率调节死区 | MONT/setGAPC2.StrVal8 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal8
4025 | setGAPC2_StrVal9_cmd | 功率调节周期 | MONT/setGAPC2.StrVal9 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal9
4026 | setGAPC2_StrVal10_cmd | 功率调节速率/功率爬坡系数 | MONT/setGAPC2.StrVal10 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal10
4027 | setGAPC2_StrVal11_cmd | SOC均衡死区 | MONT/setGAPC2.StrVal11 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal11
4028 | setGAPC2_StrVal12_cmd | 充电涓流阈值 | MONT/setGAPC2.StrVal12 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal12
4029 | setGAPC2_StrVal13_cmd | 放电涓流阈值 | MONT/setGAPC2.StrVal13 |  | yt |  |  |  | 1 | [5 empty] | setGAPC2_StrVal13
4030 | setGAPC2_StrVal14_cmd | 系统时间（秒） | MONT/setGAPC2.StrVal14 |  | yt |  |  |  | 0 | [5 empty] | setGAPC2_StrVal14
4031 | setGAPC2_StrVal15_cmd | 系统时间（分） | MONT/setGAPC2.StrVal15 |  | yt |  |  |  | 0 | [5 empty] | setGAPC2_StrVal15
4032 | setGAPC2_StrVal16_cmd | 系统时间（时） | MONT/setGAPC2.StrVal16 |  | yt |  |  |  | 0 | [5 empty] | setGAPC2_StrVal16
4033 | setGAPC3_StrVal1_cmd | 系统时间（日） | MONT/setGAPC3.StrVal1 |  | yt |  |  |  | 0 | [5 empty] | setGAPC3_StrVal1
4034 | setGAPC3_StrVal2_cmd | 系统时间（月） | MONT/setGAPC3.StrVal2 |  | yt |  |  |  | 0 | [5 empty] | setGAPC3_StrVal2
4035 | setGAPC3_StrVal3_cmd | 系统时间（年） | MONT/setGAPC3.StrVal3 |  | yt |  |  |  | 0 | [5 empty] | setGAPC3_StrVal3
4036 | setGAPC3_StrVal4_cmd | 一键对时指令 | MONT/setGAPC3.StrVal4 |  | yt |  |  |  | 0 | [5 empty] | setGAPC3_StrVal4
4037 | setGAPC3_StrVal5_cmd | 报警输出是否跳闸 | MONT/setGAPC3.StrVal5 |  | yt |  |  |  | 1 | [5 empty] | setGAPC3_StrVal5
4038 | setGAPC3_StrVal6_cmd | PCS ARM复位 | MONT/setGAPC3.StrVal6 |  | yt |  |  |  | 0 | [5 empty] | setGAPC3_StrVal6
4039 | setGAPC3_StrVal7_cmd | 子站控制器恢复出厂设置 | MONT/setGAPC3.StrVal7 |  | yt |  |  |  | 0 | [5 empty] | setGAPC3_StrVal7
4040 | setGAPC3_StrVal8_cmd | 最低高效负载率 | MONT/setGAPC3.StrVal8 |  | yt |  |  |  | 1 | [5 empty] | setGAPC3_StrVal8
4041 | setGAPC3_StrVal9_cmd | 状态切换防震荡闭锁时间 | MONT/setGAPC3.StrVal9 |  | yt |  |  |  | 1 | [5 empty] | setGAPC3_StrVal9

## source
kind | ref | dataset | trg | intg_pd | buf_tm | interval | gi | purge | enable
brcb | MONT/LLN0.BR.brcbDin* |  | dchg,period | 13000 |  |  | 1 | 0 | 1
urcb | MONT/LLN0.RP.urcbAin* |  | dchg,period | 5000 |  |  | 1 |  | 1
urcb | MONT/LLN0.RP.urcbParameter* |  | dchg,period | 15000 |  |  | 1 |  | 1

## icd_info
item | value
icd_file | INPOWER_MMS_1.5.icd
icd_sha256 | f567d390caabcf9a
ied | PCS0001
ied_desc | RS100_PCS
manufacturer | RUISHAN
access_point | S1
logical_devices | MONT
ip | 192.168.1.136
remote_ap_title | 1 3 9999 106
remote_ae_qualifier | 33
remote_psel | 00 00 00 01
remote_ssel | 00 01
remote_tsel | 00 01