## 遥测
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译 | 状态字 | 告警位
1 | PCS端口 A 相电压 | U16 | V |  | 201 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsPortAPhaseVoltage | {"en":"PCS port A-phase voltage"}
2 | PCS端口 B 相电压 | U16 | V |  | 202 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsPortBPhaseVoltage | {"en":"PCS Port B Phase Voltage"}
3 | PCS端口 C 相电压 | U16 | V |  | 203 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsPortCPhaseVoltage | {"en":"PCS port C-phase voltage"}
4 | PCS 端口 A 相电流 | I16 | A |  | 204 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsPortAPhaseCurrent | {"en":"PCS port A-phase current"}
5 | PCS 输出 B 相电流 | I16 | A |  | 205 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsOutputBPhaseCurrent | {"en":"PCS output B-phase current"}
6 | PCS 输出 C 相电流 | I16 | A |  | 206 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsOutputCPhaseCurrent | {"en":"PCS output C-phase current"}
7 | 电网频率 | U16 | Hz |  | 207 | InputRegisters | 1 | AB | 0.01 | 0 |  | gridFrequency | {"en":"grid frequency"}
8 | PCS A 相输出有功功率 | I16 | kW |  | 208 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsAPhaseOutputActivePower | {"en":"PCS A-phase output active power"}
9 | PCS B 相输出有功功率 | I16 | kW |  | 209 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsBPhaseOutputActivePower | {"en":"PCS B-phase output active power"}
10 | PCS C 相输出有功功率 | I16 | kW |  | 210 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsCPhaseOutputActivePower | {"en":"PCS C-phase output active power"}
11 | PCS 总输出有功功率 | I16 | kW |  | 211 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsTotalOutputActivePower | {"en":"PCS total output active power"}
12 | PCS A 相输出无功功率 | I16 | kVar |  | 212 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsAPhaseOutputReactivePower | {"en":"PCS A-phase output reactive power"}
13 | PCS B 相输出无功功率 | I16 | kVar |  | 213 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsBPhaseOutputReactivePower | {"en":"PCS B-phase output reactive power"}
14 | PCS C 相输出无功功率 | I16 | kVar |  | 214 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsCPhaseOutputReactivePower | {"en":"PCS C-phase output reactive power"}
15 | PCS 总输出无功功率 | I16 | kVar |  | 215 | InputRegisters | 1 | AB | 0.1 | 0 |  | totalReactivePowerOutputOfPcs | {"en":"Total reactive power output of PCS"}
16 | PCS A 相输出视在功率 | U16 | kVA |  | 216 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsAPhaseOutputApparentPower | {"en":"PCS A-phase output apparent power"}
17 | PCS B 相输出视在功率 | U16 | kVA |  | 217 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsBPhaseOutputApparentPower | {"en":"PCS B-phase output apparent power"}
18 | PCS C 相输出视在功率 | U16 | kVA |  | 218 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsCPhaseOutputApparentPower | {"en":"PCS C-phase output apparent power"}
19 | PCS 总输出视在功率 | U16 | kVA |  | 219 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsTotalOutputApparentPower | {"en":"PCS total output apparent power"}
20 | PCS 输出 A 相功率因数 | I16 |  |  | 220 | InputRegisters | 1 | AB | 0.001 | 0 |  | pcsOutputAPhasePowerFactor | {"en":"PCS output A-phase power factor"}
21 | PCS 输出 B 相功率因数 | I16 |  |  | 221 | InputRegisters | 1 | AB | 0.001 | 0 |  | pcsOutputBPhasePowerFactor | {"en":"PCS output B-phase power factor"}
22 | PCS 输出 C 相功率因数 | I16 |  |  | 222 | InputRegisters | 1 | AB | 0.001 | 0 |  | pcsOutputCPhasePowerFactor | {"en":"PCS output C-phase power factor"}
23 | PCS 输出总功率因数 | I16 |  |  | 223 | InputRegisters | 1 | AB | 0.001 | 0 |  | pcsOutputTotalPowerFactor | {"en":"PCS output total power factor"}
24 | PCS 输入功率 | I16 | kW |  | 224 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsInputPower | {"en":"PCS input power"}
25 | PCS 输入电压 | I16 | V |  | 225 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsInputVoltage | {"en":"PCS input voltage"}
26 | PCS 输入电流 | I16 | A |  | 226 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsInputCurrent | {"en":"PCS input current"}
27 | PCS 散热器温度 | I16 | °C |  | 227 | InputRegisters | 1 | AB | 1 | 0 |  | pcsRadiatorTemperature | {"en":"PCS radiator temperature"}
28 | BMS 工作状态 | U16 |  |  | 228 | InputRegisters | 1 | AB | 1 | 0 |  | bmsWorkingStatus | {"en":"BMS working status"}
29 | PCS 运行状态 | U16 |  |  | 229 | InputRegisters | 1 | AB | 1 | 0 |  | pcsOperatingStatus | {"en":"PCS operating status"}
30 | PCS 交流累计充电电量 | U32 | kWh |  | 230 | InputRegisters | 2 | CDAB | 0.001 | 0 |  | accumulatedChargingPowerOfPcsCommunication | {"en":"Accumulated charging power of PCS communication"}
31 | PCS 交流累计放电电量 | U32 | kWh |  | 232 | InputRegisters | 2 | CDAB | 0.001 | 0 |  | accumulatedDischargePowerOfPcsCommunication | {"en":"Accumulated discharge power of PCS communication"}
32 | PCS 直流累计充电电量 | U32 | kWh |  | 234 | InputRegisters | 2 | CDAB | 0.001 | 0 |  | pcsDcCumulativeChargingCapacity | {"en":"PCS DC cumulative charging capacity"}
33 | PCS 直流累计放电电量 | U32 | kWh |  | 236 | InputRegisters | 2 | CDAB | 0.001 | 0 |  | pcsDcCumulativeDischargePower | {"en":"PCS DC cumulative discharge power"}
34 | PCS 通讯状态字 | U16 |  |  | 238 | InputRegisters | 1 | AB | 1 | 0 |  | pcsCommunicationStatusWord | {"en":"PCS communication status word"}
35 | 系统时钟-秒 | U16 |  |  | 239 | InputRegisters | 1 | AB | 1 | 0 |  | systemClockSeconds | {"en":"System clock - seconds"}
36 | 系统时钟-分 | U16 |  |  | 240 | InputRegisters | 1 | AB | 1 | 0 |  | systemClockMinute | {"en":"System clock minute"}
37 | 系统时钟-时 | U16 |  |  | 241 | InputRegisters | 1 | AB | 1 | 0 |  | systemClockHour | {"en":"System clock - hour"}
38 | 系统时钟-日 | U16 |  |  | 242 | InputRegisters | 1 | AB | 1 | 0 |  | systemClockDay | {"en":"System Clock - Day"}
39 | 系统时钟-月 | U16 |  |  | 243 | InputRegisters | 1 | AB | 1 | 0 |  | systemClockMonth | {"en":"System Clock - Month"}
40 | 系统时钟-年 | U16 |  |  | 244 | InputRegisters | 1 | AB | 1 | 0 |  | systemClockYear | {"en":"System Clock - Year"}
41 | 控制软件版本 | U16 |  |  | 245 | InputRegisters | 1 | AB | 0.1 | 0 |  | controlSoftwareVersion | {"en":"Control software version"}
42 | FPGA 程序版本 | U16 |  |  | 246 | InputRegisters | 1 | AB | 1 | 0 |  | fpgaProgramVersion | {"en":"FPGA program version"}
43 | N 相电流有效值 | U16 | A |  | 247 | InputRegisters | 1 | AB | 0.1 | 0 |  | effectiveValueOfNPhaseCurrent | {"en":"Effective value of N-phase current"}
44 | PCS 状态查询码 1 | U16 |  |  | 248 | InputRegisters | 1 | AB | 1 | 0 |  | pcsStatusQueryCode1 | {"en":"PCS status query code 1"}
45 | PCS 状态查询码 2 | U16 |  |  | 249 | InputRegisters | 1 | AB | 1 | 0 |  | pcsStatusQueryCode2 | {"en":"PCS status query code 2"}
46 | PCS 状态查询码 3 | U16 |  |  | 250 | InputRegisters | 1 | AB | 1 | 0 |  | pcsStatusQueryCode3 | {"en":"PCS status query code 3"}
47 | PCS 状态查询码 4 | U16 |  |  | 251 | InputRegisters | 1 | AB | 1 | 0 |  | pcsStatusQueryCode4 | {"en":"PCS status query code 4"}
48 | PCS 状态查询码 5 | U16 |  |  | 252 | InputRegisters | 1 | AB | 1 | 0 |  | pcsStatusQueryCode5 | {"en":"PCS status query code 5"}
49 | PCS 状态查询码 6 | U16 |  |  | 253 | InputRegisters | 1 | AB | 1 | 0 |  | pcsStatusQueryCode6 | {"en":"PCS status query code 6"}
50 | PCS 状态查询码 7 | U16 |  |  | 254 | InputRegisters | 1 | AB | 1 | 0 |  | pcsStatusQueryCode7 | {"en":"PCS status query code 7"}
51 | PCS 状态查询码 8 | U16 |  |  | 255 | InputRegisters | 1 | AB | 1 | 0 |  | pcsStatusQueryCode8 | {"en":"PCS status query code 8"}
52 | PCS 故障字 5 | U16 |  |  | 256 | InputRegisters | 1 | AB | 1 | 0 |  | pcsFaultWord5 | {"en":"PCS fault word 5"}
53 | 片上 SOC 温度 | U16 |  |  | 257 | InputRegisters | 1 | AB | 0.1 | 0 |  | onChipSocTemperature | {"en":"On chip SOC temperature"}
54 | IGBT 温度 1 | U16 |  |  | 258 | InputRegisters | 1 | AB | 1 | 0 |  | igbtTemperature1 | {"en":"IGBT temperature 1"}
55 | IGBT 温度 2 | U16 |  |  | 259 | InputRegisters | 1 | AB | 1 | 0 |  | igbtTemperature2 | {"en":"IGBT temperature 2"}
56 | IGBT 温度 3 | U16 |  |  | 260 | InputRegisters | 1 | AB | 1 | 0 |  |  | {"en":""}
57 | IGBT 温度 4 | U16 |  |  | 261 | InputRegisters | 1 | AB | 1 | 0 |  | igbtTemperature4 | {"en":"IGBT temperature 4"}
58 | 通讯软件版本号 | U16 |  |  | 262 | InputRegisters | 1 | AB | 1 | 0 |  | communicationSoftwareVersionNumber | {"en":"Communication software version number"}
59 | DCDC 输入电压 | I16 | V |  | 263 | InputRegisters | 1 | AB | 0.1 | 0 |  | dcdcInputVoltage | {"en":"DCDC input voltage"}
60 | DCDC 输出电压 | I16 | V |  | 264 | InputRegisters | 1 | AB | 0.1 | 0 |  | dcdcOutputVoltage | {"en":"DCDC output voltage"}
61 | DCDC 输入电流 | I16 | A |  | 265 | InputRegisters | 1 | AB | 0.1 | 0 |  | dcdcInputCurrent | {"en":"DCDC input current"}
62 | DCDC 输出电流 | I16 | A |  | 266 | InputRegisters | 1 | AB | 0.1 | 0 |  | dcdcOutputCurrent | {"en":"DCDC output current"}
63 | DCDC 输入功率 | I16 | kW |  | 267 | InputRegisters | 1 | AB | 0.1 | 0 |  | dcdcInputPower | {"en":"DCDC input power"}
64 | DCDC 散热器温度 | I16 |  |  | 268 | InputRegisters | 1 | AB | 0.1 | 0 |  | dcdcRadiatorTemperature | {"en":"DCDC radiator temperature"}
65 | 保留 | I16 |  |  | 269 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
66 | 保留 | I16 |  |  | 270 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
67 | DCDC 程序版本 | U16 |  |  | 271 | InputRegisters | 1 | AB | 1 | 0 |  | dcdcProgramVersion | {"en":"DCDC program version"}
68 | PCS 故障字 1 | U16 |  |  | 272 | InputRegisters | 1 | AB | 1 | 0 |  | pcsFaultWord1 | {"en":"PCS fault word 1"}
69 | PCS 故障字 2 | U16 |  |  | 273 | InputRegisters | 1 | AB | 1 | 0 |  | pcsFaultWord2 | {"en":"PCS fault word 2"}
70 | PCS 故障字 3 | U16 |  |  | 274 | InputRegisters | 1 | AB | 1 | 0 |  | pcsFaultWord3 | {"en":"PCS fault word 3"}
71 | PCS 故障字 4 | U16 |  |  | 275 | InputRegisters | 1 | AB | 1 | 0 |  | pcsFaultWord4 | {"en":"PCS fault word 4"}
72 | DCDC 故障字 1 | U16 |  |  | 276 | InputRegisters | 1 | AB | 1 | 0 |  | dcdcFaultWord1 | {"en":"DCDC fault word 1"}
73 | DCDC 故障字 2 | U16 |  |  | 277 | InputRegisters | 1 | AB | 1 | 0 |  | dcdcFaultWord2 | {"en":"DCDC fault word 2"}
74 | DCDC 故障字 3 | U16 |  |  | 278 | InputRegisters | 1 | AB | 1 | 0 |  | dcdcFaultWord3 | {"en":"DCDC fault word 3"}
75 | DCDC 故障字 4 | U16 |  |  | 279 | InputRegisters | 1 | AB | 1 | 0 |  | dcdcFaultWord4 | {"en":"DCDC fault word 4"}
76 | BMS 工作指令 | U16 |  |  | 280 | InputRegisters | 1 | AB | 1 | 0 |  | bmsWorkInstructions | {"en":"BMS work instructions"}
77 | BMS 允许充电电流 | U16 | A |  | 281 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsAllowsChargingCurrent | {"en":"BMS allows charging current"}
78 | BMS 允许放电电流 | U16 | A |  | 282 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsAllowsDischargeCurrent | {"en":"BMS allows discharge current"}
79 | BMS SOC | U16 | % |  | 283 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsSoc | {"en":"BMS SOC"}
80 | BMS 可充电电量 | U16 | kWh |  | 284 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsRechargeableBatteryCapacity | {"en":"BMS rechargeable battery capacity"}
81 | BMS 可放电电量 | U16 | kWh |  | 285 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsDischargeCapacity | {"en":"BMS discharge capacity"}
82 | BMS 总电压 | U16 | V |  | 286 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsTotalVoltage | {"en":"BMS total voltage"}
83 | BMS 总电流 | I16 | A |  | 287 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsTotalCurrent | {"en":"BMS total current"}
84 | BMS 单体最高 SOC | U16 | % |  | 288 | InputRegisters | 1 | AB | 0.1 | 0 |  | maximumSocOfBmsMonomer | {"en":"Maximum SOC of BMS monomer"}
85 | BMS 单体最低 SOC | U16 | % |  | 289 | InputRegisters | 1 | AB | 0.1 | 0 |  | minimumSocOfBmsMonomer | {"en":"Minimum SOC of BMS monomer"}
86 | BMS 单体最高电压 | U16 | V |  | 290 | InputRegisters | 1 | AB | 0.1 | 0 |  | maximumVoltageOfBmsUnit | {"en":"Maximum voltage of BMS unit"}
87 | BMS 单体最低电压 | U16 | V |  | 291 | InputRegisters | 1 | AB | 0.1 | 0 |  | minimumVoltageOfBmsUnit | {"en":"Minimum voltage of BMS unit"}
88 | BMS 单体最高温度 | I16 | °C |  | 292 | InputRegisters | 1 | AB | 0.1 | 0 |  | maximumTemperatureOfBmsUnit | {"en":"Maximum temperature of BMS unit"}
89 | BMS 单体最低温度 | I16 | °C |  | 293 | InputRegisters | 1 | AB | 0.1 | 0 |  | minimumTemperatureOfBmsUnit | {"en":"Minimum temperature of BMS unit"}
90 | BMS 允许充电功率 | U16 | kW |  | 294 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsAllowsChargingPower | {"en":"BMS allows charging power"}
91 | BMS 允许放电功率 | U16 | kW |  | 295 | InputRegisters | 1 | AB | 0.1 | 0 |  | bmsAllowsDischargePower | {"en":"BMS allows discharge power"}
92 | 保留 | U16 |  |  | 296 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
93 | 保留 | U16 |  |  | 297 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
94 | 保留 | U16 |  |  | 298 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
95 | 保留 | U16 |  |  | 299 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
96 | 保留 | U16 |  |  | 300 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
97 | PCS SN 码信息 | U16 |  |  | 501 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
98 | PCS SN 码信息 | U16 |  |  | 502 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
99 | PCS SN 码信息 | U16 |  |  | 503 | InputRegisters | 1 | AB | 1 | 0 |  |  | {"en":""}
100 | PCS SN 码信息 | U16 |  |  | 504 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
101 | PCS SN 码信息 | U16 |  |  | 505 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
102 | PCS SN 码信息 | U16 |  |  | 506 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
103 | PCS SN 码信息 | U16 |  |  | 507 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
104 | PCS SN 码信息 | U16 |  |  | 508 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
105 | PCS SN 码信息 | U16 |  |  | 509 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
106 | PCS SN 码信息 | U16 |  |  | 510 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
107 | PCS SN 码信息 | U16 |  |  | 511 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
108 | PCS SN 码信息 | U16 |  |  | 512 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
109 | PCS SN 码信息 | U16 |  |  | 513 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
110 | PCS SN 码信息 | U16 |  |  | 514 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
111 | PCS SN 码信息 | U16 |  |  | 515 | InputRegisters | 1 | AB | 1 | 0 |  | pcsSnCodeInformation | {"en":"PCS SN code information"}
112 | BMS SN 码信息 | U16 |  |  | 516 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSnCodeInformation | {"en":"BMS SN code information"}
113 | BMS SN 码信息 | U16 |  |  | 517 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSnCodeInformation | {"en":"BMS SN code information"}
114 | BMS SN 码信息 | U16 |  |  | 518 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSnCodeInformation | {"en":"BMS SN code information"}
115 | BMS SN 码信息 | U16 |  |  | 519 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSnCodeInformation | {"en":"BMS SN code information"}
116 | BMS SN 码信息 | U16 |  |  | 520 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSnCodeInformation | {"en":"BMS SN code information"}
117 | BMS SN 码信息 | U16 |  |  | 521 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSnCodeInformation | {"en":"BMS SN code information"}
118 | BMS SN 码信息 | U16 |  |  | 522 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSnCodeInformation | {"en":"BMS SN code information"}
119 | BMS SN 码信息 | U16 |  |  | 523 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSnCodeInformation | {"en":"BMS SN code information"}
120 | BMS 软件版本号 | U16 |  |  | 524 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSoftwareVersionNumber | {"en":"BMS software version number"}
121 | BMS 软件版本号 | U16 |  |  | 525 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSoftwareVersionNumber | {"en":"BMS software version number"}
122 | BMS 软件版本号 | U16 |  |  | 526 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSoftwareVersionNumber | {"en":"BMS software version number"}
123 | BMS 软件版本号 | U16 |  |  | 527 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSoftwareVersionNumber | {"en":"BMS software version number"}
124 | BMS 软件版本号 | U16 |  |  | 528 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSoftwareVersionNumber | {"en":"BMS software version number"}
125 | BMS 软件版本号 | U16 |  |  | 529 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSoftwareVersionNumber | {"en":"BMS software version number"}
126 | BMS 软件版本号 | U16 |  |  | 530 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSoftwareVersionNumber | {"en":"BMS software version number"}
127 | BMS 软件版本号 | U16 |  |  | 531 | InputRegisters | 1 | AB | 1 | 0 |  | bmsSoftwareVersionNumber | {"en":"BMS software version number"}
128 | BMS 控制和状态信息 | U16 |  |  | 532 | InputRegisters | 1 | AB | 1 | 0 |  | bmsControlAndStatusInformation | {"en":"BMS control and status information"}
129 | BMS 控制和状态信息 | U16 |  |  | 533 | InputRegisters | 1 | AB | 1 | 0 |  | bmsControlAndStatusInformation | {"en":"BMS control and status information"}
130 | BMS 控制和状态信息 | U16 |  |  | 534 | InputRegisters | 1 | AB | 1 | 0 |  | bmsControlAndStatusInformation | {"en":"BMS control and status information"}
131 | BMS 控制和状态信息 | U16 |  |  | 535 | InputRegisters | 1 | AB | 1 | 0 |  | bmsControlAndStatusInformation | {"en":"BMS control and status information"}
132 | 降额系数 | U16 |  |  | 560 | InputRegisters | 1 | AB | 1 | 0 |  | deratingCoefficient | {"en":"Derating coefficient"}
133 | 降额标志 | U16 |  |  | 561 | InputRegisters | 1 | AB | 1 | 0 |  | deratingSign | {"en":"Derating sign"}
134 | PCS 电容上直压 | I16 | V |  | 562 | InputRegisters | 1 | AB | 0.1 | 0 |  | directVoltageOnPcsCapacitor | {"en":"Direct voltage on PCS capacitor"}
135 | PCS 电容下直压 | I16 | V |  | 563 | InputRegisters | 1 | AB | 0.1 | 0 |  | directVoltageUnderPcsCapacitor | {"en":"Direct voltage under PCS capacitor"}
136 | PCS 总直压 | I16 | V |  | 564 | InputRegisters | 1 | AB | 0.1 | 0 |  | pcsTotalDirectPressure | {"en":"PCS total direct pressure"}
137 | 漏电流值 | U16 | A |  | 565 | InputRegisters | 1 | AB | 0.001 | 0 |  | leakageCurrentValue | {"en":"Leakage current value"}
138 | 绝缘电阻值 | U16 | KΩ |  | 566 | InputRegisters | 1 | AB | 1 | 0 |  | insulationResistanceValue | {"en":"insulation resistance value"}
139 | A 相支路 1 电流 | I16 | A |  | 567 | InputRegisters | 1 | AB | 0.1 | 0 |  | aPhaseBranch1Current | {"en":"A-phase branch 1 current"}
140 | B 相支路 1 电流 | I16 | A |  | 568 | InputRegisters | 1 | AB | 0.1 | 0 |  | bPhaseBranch1Current | {"en":"B-phase branch 1 current"}
141 | C 相支路 1 电流 | I16 | A |  | 569 | InputRegisters | 1 | AB | 0.1 | 0 |  | currentOfCPhaseBranch1 | {"en":"Current of C-phase branch 1"}
142 | N 相支路 1 电流 | I16 | A |  | 570 | InputRegisters | 1 | AB | 0.1 | 0 |  | nPhaseBranch1Current | {"en":"N-phase branch 1 current"}
143 | A 相支路 2 电流 | I16 | A |  | 571 | InputRegisters | 1 | AB | 0.1 | 0 |  | aPhaseBranch2Current | {"en":"A-phase branch 2 current"}
144 | B 相支路 2 电流 | I16 | A |  | 572 | InputRegisters | 1 | AB | 0.1 | 0 |  | bPhaseBranch2Current | {"en":"B-phase branch 2 current"}
145 | C 相支路 2 电流 | I16 | A |  | 573 | InputRegisters | 1 | AB | 0.1 | 0 |  | cPhaseBranch2Current | {"en":"C-phase branch 2 current"}
146 | N 相支路 2 电流 | I16 | A |  | 574 | InputRegisters | 1 | AB | 0.1 | 0 |  | nPhaseBranch2Current | {"en":"N-phase branch 2 current"}
147 | A 相温度 | I16 |  |  | 600 | InputRegisters | 1 | AB | 0.01 | 0 |  | phaseATemperature | {"en":"Phase A temperature"}
148 | B 相温度 | I16 |  |  | 601 | InputRegisters | 1 | AB | 0.01 | 0 |  | bPhaseTemperature | {"en":"B-phase temperature"}
149 | C 相温度 | I16 |  |  | 602 | InputRegisters | 1 | AB | 0.01 | 0 |  | cPhaseTemperature | {"en":"C-phase temperature"}
150 | N 相温度 | I16 |  |  | 603 | InputRegisters | 1 | AB | 0.01 | 0 |  | nPhaseTemperature | {"en":"N-phase temperature"}
151 | 进风口温度 | I16 |  |  | 604 | InputRegisters | 1 | AB | 0.01 | 0 |  | inletAirTemperature | {"en":"Inlet air temperature"}
152 | 腔内温度 | I16 |  |  | 605 | InputRegisters | 1 | AB | 0.01 | 0 |  | intracavityTemperature | {"en":"intracavity temperature"}
153 | 出风口温度 | I16 |  |  | 606 | InputRegisters | 1 | AB | 0.01 | 0 |  | airOutletTemperature | {"en":"Air outlet temperature"}
154 | 控制芯片结温 | I16 |  |  | 607 | InputRegisters | 1 | AB | 0.01 | 0 |  | controlChipJunctionTemperature | {"en":"Control chip junction temperature"}
155 | 通讯芯片结温 | I16 |  |  | 608 | InputRegisters | 1 | AB | 0.01 | 0 |  | communicationChipJunctionTemperature | {"en":"Communication chip junction temperature"}
156 | PCS 控制软件故障字 1 | U16 |  |  | 609 | InputRegisters | 1 | AB | 1 | 0 |  | pcsControlSoftwareFaultWord1 | {"en":"PCS control software fault word 1"}
157 | PCS 控制软件故障字 2 | U16 |  |  | 610 | InputRegisters | 1 | AB | 1 | 0 |  | pcsControlSoftwareFaultWord2 | {"en":"PCS control software fault word 2"}
158 | PCS 控制软件故障字 3 | U16 |  |  | 611 | InputRegisters | 1 | AB | 1 | 0 |  | pcsControlSoftwareFaultWord3 | {"en":"PCS control software fault word 3"}
159 | PCS 控制软件故障字 4 | U16 |  |  | 612 | InputRegisters | 1 | AB | 1 | 0 |  | pcsControlSoftwareFaultWord4 | {"en":"PCS control software fault word 4"}
160 | PCS 控制软件故障字 5 | U16 |  |  | 613 | InputRegisters | 1 | AB | 1 | 0 |  | pcsControlSoftwareFaultWord5 | {"en":"PCS control software fault word 5"}
161 | 保留 | U16 |  |  | 614 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
162 | 保留 | U16 |  |  | 615 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
163 | 保留 | U16 |  |  | 616 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
164 | PCS 通讯软件故障字 1 | U16 |  |  | 617 | InputRegisters | 1 | AB | 1 | 0 |  | pcsCommunicationSoftwareFaultWord1 | {"en":"PCS communication software fault word 1"}
165 | PCS 通讯软件故障字 2 | U16 |  |  | 618 | InputRegisters | 1 | AB | 1 | 0 |  | pcsCommunicationSoftwareFaultWord2 | {"en":"PCS communication software fault word 2"}
166 | PCS 通讯软件故障字 3 | U16 |  |  | 619 | InputRegisters | 1 | AB | 1 | 0 |  | pcsCommunicationSoftwareFaultWord3 | {"en":"PCS communication software fault word 3"}
167 | PCS 通讯软件故障字 4 | U16 |  |  | 620 | InputRegisters | 1 | AB | 1 | 0 |  | pcsCommunicationSoftwareFaultWord4 | {"en":"PCS communication software fault word 4"}
168 | 从机 1 运行状态 | U16 |  |  | 621 | InputRegisters | 1 | AB | 1 | 0 |  | operatingStatusOfSlave1 | {"en":"Operating status of slave 1"}
169 | 从机 1 控制软件故障字 1 | U16 |  |  | 622 | InputRegisters | 1 | AB | 1 | 0 |  | slave1ControlSoftwareFaultWord1 | {"en":"Slave 1 control software fault word 1"}
170 | 从机 1 控制软件故障字 2 | U16 |  |  | 623 | InputRegisters | 1 | AB | 1 | 0 |  | slave1ControlSoftwareFaultWord2 | {"en":"Slave 1 control software fault word 2"}
171 | 从机 1 控制软件故障字 3 | U16 |  |  | 624 | InputRegisters | 1 | AB | 1 | 0 |  | slave1ControlSoftwareFaultWord3 | {"en":"Slave 1 control software fault word 3"}
172 | 从机 1 控制软件故障字 4 | U16 |  |  | 625 | InputRegisters | 1 | AB | 1 | 0 |  | slave1ControlSoftwareFaultWord4 | {"en":"Slave 1 control software fault word 4"}
173 | 从机 1 控制软件故障字 5 | U16 |  |  | 626 | InputRegisters | 1 | AB | 1 | 0 |  | slave1ControlSoftwareFaultWord5 | {"en":"Slave 1 control software fault word 5"}
174 | 保留 | U16 |  |  | 627 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
175 | 保留 | U16 |  |  | 628 | InputRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
176 | 从机 1 通讯软件故障字 1 | U16 |  |  | 629 | InputRegisters | 1 | AB | 1 | 0 |  | slave1CommunicationSoftwareFaultWord1 | {"en":"Slave 1 communication software fault word 1"}
177 | 从机 1 通讯软件故障字 2 | U16 |  |  | 630 | InputRegisters | 1 | AB | 1 | 0 |  | slave1CommunicationSoftwareFaultWord2 | {"en":"Slave 1 communication software fault word 2"}
178 | 从机 1 通讯软件故障字 3 | U16 |  |  | 631 | InputRegisters | 1 | AB | 1 | 0 |  | slave1CommunicationSoftwareFaultWord3 | {"en":"Slave 1 communication software fault word 3"}
179 | 从机 1 通讯软件故障字 4 | U16 |  |  | 632 | InputRegisters | 1 | AB | 1 | 0 |  | slave1CommunicationSoftwareFaultWord4 | {"en":"Slave 1 communication software fault word 4"}

## 遥信
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译
1000 | 停机状态 | bool |  |  | 81 | DiscreteInputs | 1 | AB | 1 | 0 |  | shutdownStatus | {"en":"Shutdown status"}
1001 | 待机状态 | bool |  |  | 82 | DiscreteInputs | 1 | AB | 1 | 0 |  | standbyMode | {"en":"standby mode"}
1002 | 运行状态 | bool |  |  | 83 | DiscreteInputs | 1 | AB | 1 | 0 |  | operatingStatus | {"en":"Operating status"}
1003 | 总故障状态 | bool |  |  | 84 | DiscreteInputs | 1 | AB | 1 | 0 |  | overallFaultStatus | {"en":"Overall fault status"}
1004 | 总报警状态 | bool |  |  | 85 | DiscreteInputs | 1 | AB | 1 | 0 |  | overallAlarmStatus | {"en":"Overall alarm status"}
1005 | 远程/就地状态 | bool |  |  | 86 | DiscreteInputs | 1 | AB | 1 | 0 |  | remoteLocalStatus | {"en":"Remote/Local Status"}
1006 | 急停输入状态 | bool |  |  | 87 | DiscreteInputs | 1 | AB | 1 | 0 |  | emergencyStopInputStatus | {"en":"Emergency stop input status"}
1007 | 并网状态 | bool |  |  | 88 | DiscreteInputs | 1 | AB | 1 | 0 |  | gridConnectedState | {"en":"grid-connected state"}
1008 | VF 离网状态 | bool |  |  | 89 | DiscreteInputs | 1 | AB | 1 | 0 |  | vfOffGridStatus | {"en":"VF off grid status"}
1009 | 过载降容 | bool |  |  | 90 | DiscreteInputs | 1 | AB | 1 | 0 |  | overloadAndCapacityReduction | {"en":"Overload and Capacity Reduction"}
1010 | 保留 | bool |  |  | 91 | DiscreteInputs | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
1011 | 保留 | bool |  |  | 92 | DiscreteInputs | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
1012 | 保留 | bool |  |  | 93 | DiscreteInputs | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
1013 | BMS 干接点输入状态 | bool |  |  | 94 | DiscreteInputs | 1 | AB | 1 | 0 |  | bmsDryContactInputStatus | {"en":"BMS dry contact input status"}
1014 | 正直流主接合闸状态 | bool |  |  | 95 | DiscreteInputs | 1 | AB | 1 | 0 |  | positiveDcMainConnectionClosedState | {"en":"Positive DC main connection closed state"}
1015 | 负直流主接合闸状态 | bool |  |  | 96 | DiscreteInputs | 1 | AB | 1 | 0 |  | negativeDcMainConnectionClosedState | {"en":"Negative DC main connection closed state"}

## 遥调
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译
2000 | 运行模式选择 | U16 |  | 0 无 1 恒流充电 2 恒压充电 3 恒功率充电 4 直流恒压模式 | 301 | HoldingRegisters | 1 | AB | 1 | 0 |  | operationModeSelection | {"en":"Operation mode selection"}
2001 | 恒压充电电压设定值 | U16 | V |  | 302 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | constantVoltageChargingVoltageSettingValue | {"en":"Constant voltage charging voltage setting value"}
2002 | 恒流充电电流设定值 | I16 | A |  | 303 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | constantCurrentChargingCurrentSettingValue | {"en":"Constant current charging current setting value"}
2003 | 恒功率有功功率期望（三相三线制） | I16 | kW |  | 304 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | constantPowerActivePowerExpectationThreePhaseThreeWireSystem | {"en":"Constant power active power expectation (three-phase three wire system)"}
2004 | 恒功率无功功率期望（三相三线制） | I16 | kVar |  | 305 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | constantPowerReactivePowerExpectationThreePhaseThreeWireSystem | {"en":"Constant power reactive power expectation (three-phase three wire system)"}
2005 | 并离网设置 | U16 |  |  | 306 | HoldingRegisters | 1 | AB | 1 | 0 |  | offGridSetting | {"en":"Off grid setting"}
2006 | 离网输出电压给定（三相三线制） | U16 | V |  | 307 | HoldingRegisters | 1 | AB | 1 | 0 |  | offGridOutputVoltageSettingThreePhaseThreeWireSystem | {"en":"Off grid output voltage setting (three-phase three wire system)"}
2007 | 离网输出频率给定 | U16 | Hz |  | 308 | HoldingRegisters | 1 | AB | 0.01 | 0 |  | offGridOutputFrequencyGiven | {"en":"Off grid output frequency given"}
2008 | 分相控制 A 相有功功率（三相四线制） | I16 | kW |  | 309 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | phaseSeparatedControlOfActivePowerInPhaseAThreePhaseFourWireSystem | {"en":"Phase separated control of active power in phase A (three-phase four wire system)"}
2009 | 分相控制 B 相有功功率（三相四线制） | I16 | kW |  | 310 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | phaseSeparatedControlOfBPhaseActivePowerThreePhaseFourWireSystem | {"en":"Phase separated control of B-phase active power (three-phase four wire system)"}
2010 | 分相控制 C 相有功功率（三相四线制） | I16 | kW |  | 311 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | phaseSeparatedControlOfCPhaseActivePowerThreePhaseFourWireSystem | {"en":"Phase separated control of C-phase active power (three-phase four wire system)"}
2011 | 分相控制 A 相无功功率（三相四线制） | I16 | kVar |  | 312 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | phaseSeparatedControlOfAPhaseReactivePowerThreePhaseFourWireSystem | {"en":"Phase separated control of A-phase reactive power (three-phase four wire system)"}
2012 | 分相控制 B 相无功功率（三相四线制） | I16 | kVar |  | 313 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | phaseSeparatedControlOfBPhaseReactivePowerThreePhaseFourWireSystem | {"en":"Phase separated control of B-phase reactive power (three-phase four wire system)"}
2013 | 分相控制 C 相无功功率（三相四线制） | I16 | kVar |  | 314 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | phaseSeparatedControlOfCPhaseReactivePowerThreePhaseFourWireSystem | {"en":"Phase separated control of C-phase reactive power (three-phase four wire system)"}
2014 | 离网输出电压分相给定 A（三相四线制） | U16 | V |  | 315 | HoldingRegisters | 1 | AB | 1 | 0 |  | offGridOutputVoltagePhaseSeparationGivenAThreePhaseFourWireSystem | {"en":"Off grid output voltage phase separation given A (three-phase four wire system)"}
2015 | 离网输出电压分相给定 B（三相四线制） | U16 | V |  | 316 | HoldingRegisters | 1 | AB | 1 | 0 |  | offGridOutputVoltagePhaseSeparationGivenBThreePhaseFourWireSystem | {"en":"Off grid output voltage phase separation given B (three-phase four wire system)"}
2016 | 离网输出电压分相给定 C（三相四线制） | U16 | V |  | 317 | HoldingRegisters | 1 | AB | 1 | 0 |  | offGridOutputVoltagePhaseSeparationGivenCThreePhaseFourWireSystem | {"en":"Off grid output voltage phase separation given C (three-phase four wire system)"}
2017 | 保留 | U16 |  |  | 318 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
2018 | 一次调频频率死区 | U16 | Hz |  | 319 | HoldingRegisters | 1 | AB | 0.01 | 0 |  | frequencyDeadZoneOfPrimaryFrequencyModulation | {"en":"Frequency dead zone of primary frequency modulation"}
2019 | 一次调频 K 值 | U16 |  |  | 320 | HoldingRegisters | 1 | AB | 0.1 | 0 |  | primaryFrequencyModulationKValue | {"en":"Primary frequency modulation K value"}
2020 | VSG 频率下垂系数 | U16 |  |  | 321 | HoldingRegisters | 1 | AB | 1 | 0 |  | vsgFrequencyDroopCoefficient | {"en":"VSG frequency droop coefficient"}
2021 | 保留 | U16 |  |  | 322 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
2022 | （STS）并离网开关运行模式 | U16 |  |  | 323 | HoldingRegisters | 1 | AB | 1 | 0 |  | stsOffGridSwitchOperationMode | {"en":"(STS) Off grid switch operation mode"}
2023 | 有功功率控制方式 | U16 |  |  | 324 | HoldingRegisters | 1 | AB | 1 | 0 |  | activePowerControlMethod | {"en":"Active power control method"}
2024 | 电池允许充电电压 | U16 | V |  | 325 | HoldingRegisters | 1 | AB | 1 | 0 |  | allowableChargingVoltageForBattery | {"en":"Allowable charging voltage for battery"}
2025 | 电池允许放电电压 | U16 | V |  | 326 | HoldingRegisters | 1 | AB | 1 | 0 |  | allowableDischargeVoltageOfBattery | {"en":"Allowable discharge voltage of battery"}
2026 | 电池允许充电电流 | U16 | A |  | 327 | HoldingRegisters | 1 | AB | 1 | 0 |  | theBatteryAllowsChargingCurrent | {"en":"The battery allows charging current"}
2027 | 电池允许放电电流 | U16 | A |  | 328 | HoldingRegisters | 1 | AB | 1 | 0 |  | allowableDischargeCurrentOfBattery | {"en":"Allowable discharge current of battery"}
2028 | 对时-秒 | U16 |  |  | 329 | HoldingRegisters | 1 | AB | 1 | 0 |  | timingSeconds | {"en":"Timing - seconds"}
2029 | 对时-分 | U16 |  |  | 330 | HoldingRegisters | 1 | AB | 1 | 0 |  | timeMinute | {"en":"Time minute"}
2030 | 对时-时 | U16 |  |  | 331 | HoldingRegisters | 1 | AB | 1 | 0 |  | timeSynchronization | {"en":"Time synchronization"}
2031 | 对时-日 | U16 |  |  | 332 | HoldingRegisters | 1 | AB | 1 | 0 |  | timeDay | {"en":"Time day"}
2032 | 对时-月 | U16 |  |  | 333 | HoldingRegisters | 1 | AB | 1 | 0 |  | timeMonth | {"en":"Time Month"}
2033 | 对时-年 | U16 |  |  | 334 | HoldingRegisters | 1 | AB | 1 | 0 |  | timeYear | {"en":"Time - Year"}
2034 | 无功功率模式 | U16 |  |  | 335 | HoldingRegisters | 1 | AB | 1 | 0 |  | reactivePowerMode | {"en":"Reactive power mode"}
2035 | 功率因素设置 | I16 |  |  | 336 | HoldingRegisters | 1 | AB | 0.001 | 0 |  | powerFactorSetting | {"en":"Power factor setting"}
2036 | 保留 | I16 |  |  | 337 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
2037 | 保留 | I16 |  |  | 338 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
2038 | 保留 | I16 |  |  | 339 | HoldingRegisters | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
2039 | 绝缘检测使能 | U16 |  |  | 340 | HoldingRegisters | 1 | AB | 1 | 0 |  | insulationDetectionEnable | {"en":"Insulation detection enable"}
2040 | 漏电流阈值设置 | U16 | A |  | 341 | HoldingRegisters | 1 | AB | 0.001 | 0 |  | leakageCurrentThresholdSetting | {"en":"Leakage current threshold setting"}
2041 | 绝缘电阻阈值设置 | U16 | KΩ |  | 342 | HoldingRegisters | 1 | AB | 1 | 0 |  | insulationResistanceThresholdSetting | {"en":"Insulation resistance threshold setting"}
2042 | 一次调频使能 | U16 |  |  | 343 | HoldingRegisters | 1 | AB | 1 | 0 |  | primaryFrequencyModulationEnable | {"en":"Primary frequency modulation enable"}

## 遥控
序号 | 点位名称 | 数据类型 | 单位 | 备注 | 寄存器地址 | 寄存器类型 | 数量 | 字节序/字序 | 系数 | 偏移量 | 启用 | 键 | 点位名称翻译
3000 | 故障复位 | bool |  |  | 1 | Coils | 1 | AB | 1 | 0 |  | faultReset | {"en":"Fault reset"}
3001 | 设备启动 | bool |  |  | 2 | Coils | 1 | AB | 1 | 0 |  | deviceStartup | {"en":"Device startup"}
3002 | 设备停机 | bool |  |  | 3 | Coils | 1 | AB | 1 | 0 |  | equipmentShutdown | {"en":"Equipment shutdown"}
3003 | 远程急停 | bool |  |  | 4 | Coils | 1 | AB | 1 | 0 |  | remoteEmergencyStop | {"en":"Remote Emergency Stop"}
3004 | 累计充电电量清零 | bool |  |  | 5 | Coils | 1 | AB | 1 | 0 |  | accumulatedChargingPowerResetToZero | {"en":"Accumulated charging power reset to zero"}
3005 | 累计放电电量清零 | bool |  |  | 6 | Coils | 1 | AB | 1 | 0 |  | accumulatedDischargePowerResetToZero | {"en":"Accumulated discharge power reset to zero"}
3006 | 远程/就地设置 | bool |  |  | 7 | Coils | 1 | AB | 1 | 0 |  | remoteLocalSettings | {"en":"Remote/Local Settings"}
3007 | 设备待机 | bool |  |  | 8 | Coils | 1 | AB | 1 | 0 |  | deviceStandby | {"en":"Device standby"}
3008 | 保留 | bool |  |  | 9 | Coils | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
3009 | 保留 | bool |  |  | 10 | Coils | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
3010 | 保留 | bool |  |  | 11 | Coils | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
3011 | 保留 | bool |  |  | 12 | Coils | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
3012 | 保留 | bool |  |  | 13 | Coils | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
3013 | 保留 | bool |  |  | 14 | Coils | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
3014 | 保留 | bool |  |  | 15 | Coils | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}
3015 | 保留 | bool |  |  | 16 | Coils | 1 | AB | 1 | 0 | 0 | retain | {"en":"retain"}